## PFC-6075
|  |  | Project Name: |  |  | Standby Hours: | 24
[6 empty] | Alarm Mins: | 5
PFC-6075R Battery & Voltage Drop Calculations |  |  | Installed By: |  |  | Batt Efficiency: | 80%
|  |  | Designed By: |  |  | SLC Type: | Class B
|  |  | Date: |  |  | NAC Source Voltage: | 20.4
| Model #: | PFC-6075R |  |  |  | Max Panel Current (amps): | 5
| Panel ID: |  |  |  | User assumes all responsibility to ensure the quantities and current draw values in this worksheet are accurate prior to submittal.
Location:
Addressable Releasing Panel |  |  |  | Standby (amps) |  | Alarm (amps) |  | Class B
Qty | Part # | Description |  | Each | Total | Each | Total | Class A
1 | PFC-6075R | Analog Addressable FACP |  | 0.13 | 0.13 | 0.22 | 0.22
|  |  |  | Panel Standby: | 0.13 | Panel Alarm: | 0.22
P-LINK (RS-485) |  |  |  | Standby |  | Alarm
| UD-1000 | DACT |  | 0.016 |  | 0.023
| RA-6075R | LCD Annunciator |  | 0.02 |  | 0.025
| RA-6500R | LCD Annunciator |  | 0.02 |  | 0.05
| LED-16 | LED Annunciator |  | 0.025 |  | 0.025
| LED-16 | LED Annunciator LED Power* |  | 0.015 |  | 0.21
| CA-6075 | Class A Module |  | 0.012 |  | 0.044
| PSN-1000(E) | Power Expander |  | 0.015 |  | 0.015
| RLY-5 | Relay Expander |  | 0.025 |  | 0.035
| RLY-5 | Relay Expander Power* |  | 0.01 |  | 0.135
| DRV-50 | LED Driver Module |  | 0.025 |  | 0.025
| DRV-50 | LED Driver Module LED Power* |  | 0.01 |  | 0.215
| FCB-1000 | Fire Communications Bridge |  | 0.025 |  | 0.025
| FIB-1000 | Fiber Interface Board |  | 0.03 |  | 0.03
| SPG-1000 | Serial Parallel Gateway |  | 0.04 |  | 0.04
|  |  | (Maximum current draw on P-Link limited to 1 Amp) | P-LINK Standby: | 0 | P-LINK Alarm: | 0
*Only enter quantity if PLINK power is being used to power devices
SLC Devices |  |  |  | Standby |  | Alarm
| PSA | Analog Photo Smoke |  | 0.000325 |  | 0.000325
| PSHA | Analog Photo Smoke/Heat |  | 0.000325 |  | 0.000325
| RHA | Analog Rate of Rise Heat |  | 0.000325 |  | 0.000325
| FHA | Analog Fixed Temp Heat |  | 0.000325 |  | 0.000325
| DDA | Addressable Duct Detector |  | 0.000325 |  | 0.000325
| APS-SA/APS-DA | Addressable Pull Station Single/Dual Action |  | 0.000325 |  | 0.000325
| MCM | Mini Contact Input Module |  | 0.000325 |  | 0.000325
| SCM-4 | Single Contact Input Module |  | 0.000325 |  | 0.001
| DCM-4 | Dual Contact Input Module |  | 0.000325 |  | 0.001
| TRM-4 | Twin Relay Output Module |  | 0.000325 |  | 0.001
| CIZM-4 * | Conventional Zone Input Mod |  | 0.000325 |  | 0.001
| MOM-4 * | Monitored Output Module |  | 0.000325 |  | 0.001
| ARB * | Detector Base w/Relay |  | 0.000325 |  | 0.000325
| ASB * | Detector Base w/Sounder |  | 0.000325 |  | 0.000325
| SCI ** | Short Circuit Isolator (Class A) |  | 0.000325 |  | 0.00234
| AIB ** | Detector Base w/Isolator (Class A) |  | 0.000325 |  | 0.00234
| SCI/AIB Class B ** | Current Draw from Install Manual
1 |  | SLC Loop Alarm LED Current |  | 0 | 0 | 0.027 | 0.027
* | Requires Aux Power (Configure Below) |  |  | SLC Standby: | 0 | SLC Alarm: | 0.027
** | See the installation manual for special considerations when installing AIB, SCI devices on Class B loops.
NAC Circuits (See NAC Configuration below) |  |  |  |  | Standby (amps) |  | Alarm (amps)
Ckt | Use | Description |  |  | Total |  | Total
1 |  |  |  |  | 0 |  | 0
2 |  |  |  |  | 0 |  | 0
|  |  |  | NAC Standby: | 0 | NAC Alarm: | 0
I/O Circuits (See I/O Configuration below) |  |  |  |  | Standby (amps) |  | Alarm (amps)
Ckt | Use | Description |  |  | Total |  | Total
1 |  |  |  |  | 0 |  | 0
2 |  |  |  |  | 0 |  | 0
|  |  |  | I/O Standby: | 0 | I/O Alarm: | 0
| Battery Calculation Summary |  |  |  | Standby (amps) |  | Alarm (amps)
|  |  |  | Panel Current: | 0.13 |  | 0.22
|  |  |  | P-Link Current: | 0 |  | 0
|  |  |  | SLC Device Current: | 0 |  | 0.027
|  |  |  | NAC Circuit Current: | 0 |  | 0
|  |  |  | I/O Circuit Current: | 0 |  | 0
| SLC Loop Type: | Class B |  | Total Standby: | 0.13 | Total Alarm: | 0.247
| Point Capacity Needed: | 0 |  | Standby Hours: | 24 | Alarm Mins: | 5
| Point Capacity Actual: | 75 |  | AH Required: | 3.12 | AH Required: | 0.03
Releasing
[6 empty] | Total Combined Standby & Alarm AmpHours Required: | 3.15 | Aux Power
[6 empty] | Efficiency Factor: | 80% | Notification
[6 empty] | Required Battery AmpHours: | 3.9375 | Door Holders
[6 empty] | Battery AmpHours Provided: |  | Doors (Low AC Drop)
|  |  |  | Note: The cabinet will house two 8 AH or 18 AH batteries. The charging circuit is rated for up to two 55 AH batteries. |  |  |  | City Tie
Unused
NAC Circuit Configuration & Voltage Drop
Releasing
NAC 1 |  |  | MAX Circuit Current (amps): | 3 |  | Source Voltage Used (VDC): | 20.4 | Aux Power
Notification
| Usage: |  |  | Description: |  |  |  | Door Holders
Doors (Low AC Drop)
| Wire Type | Ohms/1000ft | Length 1-Way | Actual Ohms | Max Load (amps) | Volts @ EOL | Min Volts Req'd | City Tie
| #14 Solid | 2.5 |  | 0 | 0 | 20.4 | 16 | Contact Input
Polarity Reversal
Circuit Devices |  |  |  | Standby (amps) |  | Alarm (amps) |  | Unused
Qty | Lookup Type | Desc |  | Each | Total | Each | Total
Horn Strobes
Strobes
Horns
MiniHorns
Other Notification
|  | User can add devices on the fly | [5 empty] | SLC Aux Power
|  | to these bottom 5 rows | [5 empty] | Conv Detectors
|  | (No lookup function) | [5 empty] | PLINK Devices
User Defined
|  |  |  | Total Standby: | 0 | Total Alarm: | 0
[8 empty] | #12 Solid | 1.6
[8 empty] | #14 Solid | 2.5
NAC 2 |  |  | MAX Circuit Current (amps): | 3 |  | Source Voltage Used (VDC): | 20.4 | #14 Stranded | 2.5
[8 empty] | #16 Solid | 4
| Usage: |  |  | Description: |  |  |  | #16 Stranded | 4
[8 empty] | #18 Solid | 6.4
| Wire Type | Ohms/1000ft | Length 1-Way | Actual Ohms | Max Load (amps) | Volts @ EOL | Min Volts Req'd | #18 Stranded | 6.4
| #14 Solid | 2.5 |  | 0 | 0 | 20.4 | 16
Circuit Devices |  |  |  | Standby (amps) |  | Alarm (amps)
Qty | Lookup Type | Desc |  | Each | Total | Each | Total
User can add devices on the fly
to these bottom 5 rows
(No lookup function)
|  |  |  | Total Standby: | 0 | Total Alarm: | 0
I/O Circuit Configuration & Voltage Drop
I/O 1 |  |  | MAX Circuit Current (amps): | 1 |  | Source Voltage Used (VDC): | 20.4
| Usage: |  |  | Description:
| Wire Type | Ohms/1000ft | Length 1-Way | Actual Ohms | Max Load (amps) | Volts @ EOL | Min Volts Req'd
| #14 Solid | 2.5 |  | 0 | 0 | 20.4 | 16
Circuit Devices |  |  |  | Standby (amps) |  | Alarm (amps)
Qty | Lookup Type | Desc |  | Each | Total | Each | Total
User can add devices on the fly
to these bottom 5 rows
(No lookup function)
|  |  |  | Total Standby: | 0 | Total Alarm: | 0
I/O 2 |  |  | MAX Circuit Current (amps): | 1 |  | Source Voltage Used (VDC): | 20.4
| Usage: |  |  | Description:
| Wire Type | Ohms/1000ft | Length 1-Way | Actual Ohms | Max Load (amps) | Volts @ EOL | Min Volts Req'd
| #14 Solid | 2.5 |  | 0 | 0 | 20.4 | 16
Circuit Devices |  |  |  | Standby (amps) |  | Alarm (amps)
Qty | Lookup Type | Desc |  | Each | Total | Each | Total
User can add devices on the fly
to these bottom 5 rows
(No lookup function)
|  |  |  | Total Standby: | 0 | Total Alarm: | 0
Note on I101: Enter the lowest minimum voltage required to operate any of the devices on this circuit.
Note on I123: Enter the lowest minimum voltage required to operate any of the devices on this circuit.
Note on I148: Enter the lowest minimum voltage required to operate any of the devices on this circuit.
Note on I170: Enter the lowest minimum voltage required to operate any of the devices on this circuit.

## Device Database (hidden)
Horn Strobes
(Current draws listed are 2400/3000HZ Temporal audible setting)
Description | Standby | Alarm
Potter HS-24, 15cd, Hi db | 0 | 0.07
Potter HS-24, 30cd, Hi db | 0 | 0.086
Potter HS-24, 60cd, Hi db | 0 | 0.125
Potter HS-24, 75cd, Hi db | 0 | 0.144
Potter HS-24, 110cd, Hi db | 0 | 0.189
Potter HS24-177,177cd, Hi db | 0 | 0.241
Potter CHS-24, 15cd, Hi db | 0 | 0.143
Potter CHS-24, 30cd, Hi db | 0 | 0.143
Potter CHS-24, 75cd, Hi db | 0 | 0.223
Potter CHS-24. 95cd, Hi db | 0 | 0.243
Potter CHS-24, 115cd, Hi db | 0 | 0.313
Potter CHS-24, 150cd, Hi db | 0 | 0.344
Potter CHS-24A, 15cd, Hi db | 0 | 0.75
Potter CHS-24A, 30cd, Hi db | 0 | 0.92
Potter CHS-24A, 60cd, Hi db | 0 | 0.141
Potter CHS-24A, 75cd, Hi db | 0 | 0.173
Potter CHS-24A, 110cd, Hi db | 0 | 0.206
Potter CHS-24B,CHS-24G,CHS-24R, 15cd, Hi db | 0 | 0.133
Potter CHS-24B,CHS-24G,CHS-24R, 30cd, Hi db | 0 | 0.158
Potter CHS-24B,CHS-24G,CHS-24R, 60cd, Hi db | 0 | 0.231
Potter CHS-24B,CHS-24G,CHS-24R, 75cd, Hi db | 0 | 0.271
Potter CHS-24B,CHS-24G,CHS-24R, 110cd, Hi db | 0 | 0.338
Potter CCHS-24A,CCHS-24B,CCHS-24G, 15cd, Hi db | 0 | 0.147
Potter CCHS-24A,CCHS-24B,CCHS-24G, 30cd, Hi db | 0 | 0.147
Potter CCHS-24A,CCHS-24B,CCHS-24G, 75cd, Hi db | 0 | 0.162
Potter CCHS-24A,CCHS-24B,CCHS-24G, 95cd, Hi db | 0 | 0.228
Potter CCHS-24A,CCHS-24B,CCHS-24G, 115cd, Hi db | 0 | 0.235
Potter CCHS-24R, 15cd, Hi db | 0 | 0.147
Potter CCHS-24R, 30cd, Hi db | 0 | 0.147
Potter CCHS-24R, 75cd, Hi db | 0 | 0.235
Potter CCHS-24R, 95cd, Hi db | 0 | 0.306
Potter CCHS-24R, 115cd, Hi db | 0 | 0.336
Potter HS-24-WP, HSLP-24-WP 75cd, Hi db | 0 | 0.198
Potter LFHS-15 Temporal 3 Normal db | 0 | 0.124
Potter LFHS-15 Temporal 3 Loud db | 0 | 0.182
Potter LFHS-15 Temporal 4 Normal db | 0 | 0.195
Potter LFHS-15 Temporal 4 Loud db | 0 | 0.291
Potter LFHS-110 Temporal 3 Normal db | 0 | 0.28
Potter LFHS-110 Temporal 3 Loud db | 0 | 0.326
Potter LFHS-110 Temporal 4 Normal db | 0 | 0.384
Potter LFHS-110 Temporal 4 Loud db | 0 | 0.474
Potter LFHS-177 Temporal 3 Normal db | 0 | 0.365
Potter LFHS-177 Temporal 3 Loud db | 0 | 0.393
Potter LFHS-177 Temporal 4 Normal db | 0 | 0.427
Potter LFHS-177 Temporal 4 Loud db | 0 | 0.525
Potter CHS-24A-WP,CHSLP-24A-WP 75cd, Hi db | 0 | 0.198
CHS-24B-WP,CHS-24G-WP,CSH-24R-WP, 75cd, Hi db | 0 | 0.192
CHSLP-24B-WP,CHSLP-24G-WP,CHSLP-24R-WP, 75cd, Hi db | 0 | 0.192
Potter SH-1224 15cd, Hi db | 0 | 0.149
Potter SH-1224 15cd, Med db | 0 | 0.092
Potter SH-1224 15cd, Lo db | 0 | 0.08
Potter SH-1224 35cd, Hi db | 0 | 0.189
Potter SH-1224 35cd, Med db | 0 | 0.132
Potter SH-1224 35cd, Lo db | 0 | 0.12
Potter SH-1224 60cd, Hi db | 0 | 0.218
Potter SH-1224 60cd, Med db | 0 | 0.161
Potter SH-1224 60cd, Lo db | 0 | 0.149
Potter SH-1224 75cd, Hi db | 0 | 0.233
Potter SH-1224 75cd, Med db | 0 | 0.176
Potter SH-1224 75cd, Lo db | 0 | 0.164
Potter SH-1224 95cd, Hi db | 0 | 0.264
Potter SH-1224 95cd, Med db | 0 | 0.207
Potter SH-1224 95cd, Lo db | 0 | 0.195
Potter SH-1224 110cd, Hi db | 0 | 0.283
Potter SH-1224 110cd, Med db | 0 | 0.226
Potter SH-1224 110cd, Lo db | 0 | 0.214
Potter SH-1224WP 15cd, Hi db | 0 | 0.303
Potter SH-1224WP 15cd, Med db | 0 | 0.21
Potter SH-1224WP 15cd, Lo db | 0 | 0.182
Potter SH-1224WP 35cd, Hi db | 0 | 0.338
Potter SH-1224WP 35cd, Med db | 0 | 0.245
Potter SH-1224WP 35cd, Lo db | 0 | 0.217
Potter SH-1224WP 60cd, Hi db | 0 | 0.374
Potter SH-1224WP 60cd, Med db | 0 | 0.281
Potter SH-1224WP 60cd, Lo db | 0 | 0.253
Potter SH-1224WP 75cd, Hi db | 0 | 0.393
Potter SH-1224WP 75cd, Med db | 0 | 0.3
Potter SH-1224WP 75cd, Lo db | 0 | 0.272
Potter SH-1224WP 95cd, Hi db | 0 | 0.414
Potter SH-1224WP 95cd, Med db | 0 | 0.321
Potter SH-1224WP 95cd, Lo db | 0 | 0.293
Potter SH-1224WP 110cd, Hi db | 0 | 0.428
Potter SH-1224WP 110cd, Med db | 0 | 0.335
Potter SH-1224WP 110cd, Lo db | 0 | 0.307
Potter SH-24H 95cd, Hi db | 0 | 0.238
Potter SH-24H 95cd, Med db | 0 | 0.181
Potter SH-24H 95cd, Lo db | 0 | 0.169
Potter SH-24H 110cd, Hi db | 0 | 0.248
Potter SH-24H 110cd, Med db | 0 | 0.191
Potter SH-24H 110cd, Lo db | 0 | 0.179
Potter SH-24H 135cd, Hi db | 0 | 0.265
Potter SH-24H 135cd, Med db | 0 | 0.208
Potter SH-24H 135cd, Lo db | 0 | 0.196
Potter SH-24H 150cd, Hi db | 0 | 0.277
Potter SH-24H 150cd, Med db | 0 | 0.22
Potter SH-24H 150cd, Lo db | 0 | 0.208
Potter SH-24H 177cd, Hi db | 0 | 0.305
Potter SH-24H 177cd, Med db | 0 | 0.248
Potter SH-24H 177cd, Lo db | 0 | 0.236
Potter SH-24H 185cd, Hi db | 0 | 0.313
Potter SH-24H 185cd, Med db | 0 | 0.256
Potter SH-24H 185cd, Lo db | 0 | 0.244
Potter SH-24H-WP 95cd, Hi db | 0 | 0.238
Potter SH-24H-WP 95cd, Med db | 0 | 0.181
Potter SH-24H-WP 95cd, Lo db | 0 | 0.169
Potter SH-24H-WP 110cd, Hi db | 0 | 0.248
Potter SH-24H-WP 110cd, Med db | 0 | 0.191
Potter SH-24H-WP 110cd, Lo db | 0 | 0.179
Potter SH-24H-WP 135cd, Hi db | 0 | 0.265
Potter SH-24H-WP 135cd, Med db | 0 | 0.208
Potter SH-24H-WP 135cd, Lo db | 0 | 0.196
Potter SH-24H-WP 150cd, Hi db | 0 | 0.277
Potter SH-24H-WP 150cd, Med db | 0 | 0.22
Potter SH-24H-WP 150cd, Lo db | 0 | 0.208
Potter SH-24H-WP 177cd, Hi db | 0 | 0.305
Potter SH-24H-WP 177cd, Med db | 0 | 0.248
Potter SH-24H-WP 177cd, Lo db | 0 | 0.236
Potter SH-24H-WP 185cd, Hi db | 0 | 0.313
Potter SH-24H-WP 185cd, Med db | 0 | 0.256
Potter SH-24H-WP 185cd, Lo db | 0 | 0.244
Potter SH24C-3075110 30cd, Hi db | 0 | 0.16
Potter SH24C-3075110 30cd, Lo db | 0 | 0.138
Potter SH24C-3075110 75cd, Hi db | 0 | 0.218
Potter SH24C-3075110 75cd, Lo db | 0 | 0.201
Potter SH24C-3075110 110cd, Hi db | 0 | 0.273
Potter SH24C-3075110 110cd, Lo db | 0 | 0.256
Potter SH24C-177, 177cd, Hi db | 0 | 0.419
Potter SH24C-177, 177cd, Lo db | 0 | 0.402
Gentex GHSLF-15 Temporal 3 Normal db | 0 | 0.124
Gentex GHSLF-15 Temporal 3 Loud db | 0 | 0.182
Gentex GHSLF-15 Temporal 4 Normal db | 0 | 0.195
Gentex GHSLF-15 Temporal 4 Loud db | 0 | 0.291
Gentex GHSLF-110 Temporal 3 Normal db | 0 | 0.28
Gentex GHSLF-110 Temporal 3 Loud db | 0 | 0.326
Gentex GHSLF-110 Temporal 4 Normal db | 0 | 0.384
Gentex GHSLF-110 Temporal 4 Loud db | 0 | 0.474
Gentex GHSLF-177 Temporal 3 Normal db | 0 | 0.365
Gentex GHSLF-177 Temporal 3 Loud db | 0 | 0.393
Gentex GHSLF-177 Temporal 4 Normal db | 0 | 0.427
Gentex GHSLF-177 Temporal 4 Loud db | 0 | 0.525
Strobes
Description | Standby | Alarm
Potter SL-1224 Strobe 15cd | 0 | 0.061
Potter SL-1224 Strobe 35cd | 0 | 0.101
Potter SL-1224 Strobe 60cd | 0 | 0.131
Potter SL-1224 Strobe 75cd | 0 | 0.145
Potter SL-1224 Strobe 95cd | 0 | 0.176
Potter SL-1224 Strobe 110cd | 0 | 0.196
Potter SL-1224WP Strobe 15cd | 0 | 0.1
Potter SL-1224WP Strobe 35cd | 0 | 0.135
Potter SL-1224WP Strobe 60cd | 0 | 0.171
Potter SL-1224WP Strobe 75cd | 0 | 0.19
Potter SL-1224WP Strobe 95cd | 0 | 0.211
Potter SL-1224WP Strobe 110cd | 0 | 0.225
Potter SL-24H Strobe 95cd | 0 | 0.151
Potter SL-24H Strobe 110cd | 0 | 0.161
Potter SL-24H Strobe 135cd | 0 | 0.178
Potter SL-24H Strobe 150cd | 0 | 0.19
Potter SL-24H Strobe 177cd | 0 | 0.218
Potter SL-24H Strobe 185cd | 0 | 0.226
Potter SL-24H-WP Strobe 95cd | 0 | 0.151
Potter SL-24H-WP Strobe 110cd | 0 | 0.161
Potter SL-24H-WP Strobe 135cd | 0 | 0.178
Potter SL-24H-WP Strobe 150cd | 0 | 0.19
Potter SL-24H-WP Strobe 177cd | 0 | 0.218
Potter SL-24H-WP Strobe 185cd | 0 | 0.226
Potter SL24C-3075110 Strobe 30cd | 0 | 0.116
Potter SL24C-3075110 Strobe 75cd | 0 | 0.172
Potter SL24C-3075110 Strobe 110cd | 0 | 0.234
Potter SL24C-177 Strobe 177cd | 0 | 0.347
Potter S-24 Strobe, 15cd | 0 | 0.042
Potter S-24 Strobe, 30cd | 0 | 0.058
Potter S-24 Strobe, 60cd | 0 | 0.097
Potter S-24 Strobe, 75cd | 0 | 0.116
Potter S-24 Strobe, 110cd | 0 | 0.161
Potter S24-177 Strobe, 177cd | 0 | 0.213
Potter CS-24 Strobe, 15cd | 0 | 0.12
Potter CS-24 Strobe, 30cd | 0 | 0.12
Potter CS-24 Strobe, 75cd | 0 | 0.2
Potter CS-24 Strobe, 95cd | 0 | 0.22
Potter CS-24 Strobe, 115cd | 0 | 0.29
Potter CS-24 Strobe, 150cd | 0 | 0.321
Potter S-24-WP Strobe, 75cd | 0 | 0.17
Potter CS-24WA Strobe, 15cd | 0 | 0.047
Potter CS-24WA Strobe, 30cd | 0 | 0.064
Potter CS-24WA Strobe, 60cd | 0 | 0.113
Potter CS-24WA Strobe,75cd | 0 | 0.145
Potter CS-24WA Strobe,110cd | 0 | 0.178
Potter CS-24WB,CS-24WG,CS-24WR Strobe, 15cd | 0 | 0.105
Potter CS-24WB,CS-24WG,CS-24WR Strobe, 30cd | 0 | 0.13
Potter CS-24WB,CS-24WG,CS-24WR Strobe, 60cd | 0 | 0.203
Potter CS-24WB,CS-24WG,CS-24WR Strobe, 75cd | 0 | 0.243
Potter CS-24WB,CS-24WG,CS-24WR Strobe, 110cd | 0 | 0.31
Potter CCS-24A,CCS-24B,CCS-24G Strobe, 15cd | 0 | 0.124
Potter CCS-24A,CCS-24B,CCS-24G Strobe, 30cd | 0 | 0.124
Potter CCS-24A,CCS-24B,CCS-24G Strobe, 75cd | 0 | 0.139
Potter CCS-24A,CCS-24B,CCS-24G Strobe, 95cd | 0 | 0.205
Potter CCS-24A,CCS-24B,CCS-24G Strobe, 115cd | 0 | 0.212
Potter CCS-24R Strobe, 15cd | 0 | 0.124
Potter CCS-24R Strobe, 30cd | 0 | 0.124
Potter CCS-24R Strobe, 75cd | 0 | 0.212
Potter CCS-24R Strobe, 95cd | 0 | 0.283
Potter CCS-24R Strobe, 110cd | 0 | 0.313
Potter CCS-24R Strobe, 75cd | 0 | 0.17
CS-24A-WP,CS-24B-WP,CS-24G-WP,CS-24R-WP Strobe, 75cd | 0 | 0.164
CSLP-24A-WP,CS-24B-WP,CS-24G-WP,CS-24R-WP Strobe, 75cd | 0 | 0.164
Potter SPKSTR-24WLP, 15cd | 0 | 0.078
Potter SPKSTR-24WLP Strobe, 30cd | 0 | 0.096
Potter SPKSTR-24WLP Strobe, 60cd | 0 | 0.137
Potter SPKSTR-24WLP Strobe, 75cd | 0 | 0.18
Potter SPKSTR-24WLP Strobe, 110cd | 0 | 0.224
Potter SPKSTR-24CLP Strobe 15cd | 0 | 0.12
Potter SPKSTR-24CLP Strobe, 30cd | 0 | 0.12
Potter SPKSTR-24CLP Strobe, 75cd | 0 | 0.2
Potter SPKSTR-24CLP Strobe, 95cd | 0 | 0.22
Potter SPKSTR-24CLP Strobe, 115cd | 0 | 0.29
Potter CSPKSTR-24A Strobe, 15/75cd | 0 | 0.148
Potter CSPKSTR-24B Strobe, 15/75cd | 0 | 0.28
Potter CSPKSTR-24G Strobe, 15/75cd | 0 | 0.36
Potter CSPKSTR-24R Strobe, 15/75cd | 0 | 0.397
Gentex GES3-24 Strobe, 15cd | 0 | 0.042
Gentex GES3-24 Strobe, 30cd | 0 | 0.058
Gentex GES3-24 Strobe, 60cd | 0 | 0.097
Gentex GES3-24 Strobe, 75cd | 0 | 0.116
Gentex GES3-24 Strobe, 110cd | 0 | 0.161
Gentex GES24-177 Strobe, 177cd | 0 | 0.213
Gentex GCS24 Strobe, 15cd | 0 | 0.12
Gentex GCS24 Strobe, 30cd | 0 | 0.12
Gentex GCS24 Strobe, 75cd | 0 | 0.2
Gentex GCS24 Strobe, 95cd | 0 | 0.22
Gentex GCS24 Strobe, 115cd | 0 | 0.29
Gentex GCS24 Strobe, 150cd | 0 | 0.321
Gentex WGES24-75 Strobe, 75cd | 0 | 0.17
Gentex GESA24 Strobe, 15cd | 0 | 0.047
Gentex GESA24 Strobe, 30cd | 0 | 0.064
Gentex GESA24 Strobe, 60cd | 0 | 0.113
Gentex GESA24 Strobe,75cd | 0 | 0.145
Gentex GESA24 Strobe,110cd | 0 | 0.178
Gentex GESB24, GESG24, GESR24 Strobe, 15cd | 0 | 0.105
Gentex GESB24, GESG24, GESR24 Strobe, 30cd | 0 | 0.13
Gentex GESB24, GESG24, GESR24 Strobe, 60cd | 0 | 0.203
Gentex GESB24, GESG24, GESR24 Strobe, 75cd | 0 | 0.243
Gentex GESB24, GESG24, GESR24 Strobe, 110cd | 0 | 0.31
Gentex GCSA24, GCSB24, GCSG24 Strobe, 15cd | 0 | 0.124
Gentex GCSA24, GCSB24, GCSG24 Strobe, 30cd | 0 | 0.124
Gentex GCSA24, GCSB24, GCSG24 Strobe, 75cd | 0 | 0.139
Gentex GCSA24, GCSB24, GCSG24 Strobe, 95cd | 0 | 0.205
Gentex GCSA24, GCSB24, GCSG24 Strobe, 115cd | 0 | 0.212
Gentex GCSR24 Strobe, 15cd | 0 | 0.124
Gentex GCSR24 Strobe, 30cd | 0 | 0.124
Gentex GCSR24 Strobe, 75cd | 0 | 0.212
Gentex GCSR24 Strobe, 95cd | 0 | 0.283
Gentex GCSR24 Strobe, 110cd | 0 | 0.313
Gentex WGESA24 Strobe, 75cd | 0 | 0.17
Gentex WGESB24, WGESG24, WGESR24 Strobe, 75cd | 0 | 0.164
Gentex SSPK24WLP Strobe, 15cd | 0 | 0.078
Gentex SSPK24WLP Strobe, 30cd | 0 | 0.096
Gentex SSPK24WLP Strobe, 60cd | 0 | 0.137
Gentex SSPK24WLP Strobe, 75cd | 0 | 0.18
Gentex SSPK24WLP Strobe, 110cd | 0 | 0.224
Gentex SSPK24CLP Strobe, 15cd | 0 | 0.12
Gentex SSPK24CLP Strobe, 30cd | 0 | 0.12
Gentex SSPK24CLP Strobe, 75cd | 0 | 0.2
Gentex SSPK24CLP Strobe, 95cd | 0 | 0.22
Gentex SSPK24CLP Strobe, 115cd | 0 | 0.29
Gentex SSPKA24 Strobe, 15/75cd | 0 | 0.148
Gentex SSPKB24 Strobe, 15/75cd | 0 | 0.28
Gentex SSPKG24 Strobe, 15/75cd | 0 | 0.36
Gentex SSPKR24 Strobe, 15/75cd | 0 | 0.397
Horns
Description | Standby | Alarm
Potter H-1224 Horn, Hi db | 0 | 0.087
Potter H-1224 Horn, Med db | 0 | 0.03
Potter H-1224 Horn, Lo db | 0 | 0.018
Potter EH-24 Horn, High db | 0 | 0.029
Potter LFH-24 LF Horn, Temporal 3 Normal db | 0 | 0.0994
Potter LFH-24 LF Horn, Temporal 3 Loud db | 0 | 0.1558
Potter LFH-24 LF Horn, Temporal 4 Normal db | 0 | 0.1001
Potter LFH-24 LF Horn, Temporal 4 Loud db | 0 | 0.1572
Gentex GEH24 Horn, High db | 0 | 0.029
Gentex GHLF LF Horn, Temporal 3 Normal db | 0 | 0.0994
Gentex GHLF LF Horn, Temporal 3 Loud db | 0 | 0.1558
Gentex GHLF LF Horn, Temporal 4 Normal db | 0 | 0.1001
Gentex GHLF LF Horn, Temporal 4 Loud db | 0 | 0.1572
MiniHorns
Description | Standby | Alarm
Potter HP-25T MiniHorn, Synchable | 0 | 0.0164
Potter MH-12/24 MiniHorn | 0 | 0.015
Potter MHT-1224 Mini Horn | 0 | 0.018
Gentex GX-93 Mini Horn | 0 | 0.018
Other Notification
Description | Standby | Alarm
Potter MBA-246 Bell | 0 | 0.06
Potter MBA-248 Bell | 0 | 0.06
Potter MBA-2410 Bell | 0 | 0.06
Federal FHEX Explsn Proof Horn | 0 | 1.2
Federal FSEX Explsn Proof Strobe | 0 | 1.9
SLC Aux Power
Description | Standby | Alarm
Potter ARB-6 Det Base w/Relay | 0.005 | 0.05
Potter ASB Det Base w/Sounder | 0.005 | 0.1
Potter CIZM-4 Conv Zone Class A | 0.0049 | 0.05
Potter CIZM-4 Conv Zone Class B | 0.0085 | 0.05
Potter MOM-4 Output Module | 0.0016 | 0.0016
Conventional Detectors
Description | Standby | Alarm
Potter DSD-P Duct Detector | 0.013 | 0.06
Potter CO-12/24 CO Detector | 6e-05 | 0.08
Potter PS-24 Photo Smoke Det | 4.5e-05 | 0.16
Potter PS-24H Photo/Heat Det | 4.5e-05 | 0.16
PLINK Devices
Description | Standby | Alarm
DRV-50 LED Power | 0.01 | 0.215
RLY-5 Power | 0.01 | 0.135
LED-16 LED Power | 0.015 | 0.21

## User Defined
User Defined Parts
Description | Standby | Alarm
User Defined 1
User Defined 2
User Defined 3
User Defined 4
User Defined 5
User Defined 6
User Defined 7
User Defined 8
User Defined 9
User Defined 10
User Defined 11
User Defined 12
User Defined 13
User Defined 14
User Defined 15
User Defined 16
User Defined 17
User Defined 18
User Defined 19
User Defined 20
User Defined 21
User Defined 22
User Defined 23
User Defined 24
User Defined 25
User Defined 26
User Defined 27
User Defined 28
User Defined 29
User Defined 30
User Defined 31
User Defined 32
User Defined 33
User Defined 34
User Defined 35
User Defined 36
User Defined 37
User Defined 38
User Defined 39
User Defined 40
User Defined 41
User Defined 42
User Defined 43
User Defined 44
User Defined 45
User Defined 46
User Defined 47
User Defined 48
User Defined 49
User Defined 50
User Defined 51
User Defined 52
User Defined 53
User Defined 54
User Defined 55
User Defined 56
User Defined 57
User Defined 58
User Defined 59
User Defined 60
User Defined 61
User Defined 62
User Defined 63
User Defined 64
User Defined 65
User Defined 66
User Defined 67
User Defined 68
User Defined 69
User Defined 70
User Defined 71
User Defined 72
User Defined 73
User Defined 74
User Defined 75
User Defined 76
User Defined 77
User Defined 78
User Defined 79
User Defined 80
User Defined 81
User Defined 82
User Defined 83
User Defined 84
User Defined 85
User Defined 86
User Defined 87
User Defined 88
User Defined 89
User Defined 90
User Defined 91
User Defined 92
User Defined 93
User Defined 94
User Defined 95
User Defined 96
User Defined 97
User Defined 98
User Defined 99
User Defined 100