## Main
Potter Electric Signal Company, LLC
Tech Ph: 866-956-1211 • www.pottersignal.com
PFC-8000 Series Battery Calculation Worksheet
| QTY | Device | Standby Current |  | Alarm Current
|  |  | Each | Total | Each | Total
| 1 | PFC-8060 60 Point Analog Addressable Panel | 0.172 | 0.172 | 0.272 | 0.272 | 60
| Total Standby Current: |  |  | 0.172 | Alarm: | 0.272
Fire Alarm Panel Components
|  |  | 0.0 |  | 0.0 |  | 0
|  | Total Standby Current: |  | 0 | Alarm: | 0 | 60
Addressable Modules & Short Circuit Isolator
|  | MCM Mini Contact Module | 0.00025 |  | 0.00025 |  | 0
|  | SCM-4 Single Contact Module | 0.00025 |  | 0.00025 |  | 0
|  | DCM-4 Dual Contact Module | #N/A |  | 0.00025 |  | 0
|  | CIZM-4 Conventional Input Zone Module | 0.00025 |  | 0.00025 |  | 0
|  | TRM-4 Twin Relay Module | 0.00025 |  | 0.00025 |  | 0
|  | MOM-4 Monitored Output Module | 0.00025 |  | 0.00025 |  | 0
|  | SCI Short Circuit Isolator | 0.00025 |  | 0.00025 |  | 0
| 0 | Total Standby Current: |  | 0 | Alarm: | 0 | 0
Initiating Devices & Bases
|  | PSA Analog Photoelectric Smoke Detector | 0.00025 |  | 0.00025 |  | 0
|  | PSHA Analog Combination Photoelectric Smoke & Heat Detector | 0.00025 |  | 0.00025 |  | 0
|  | DSA Analog Duct Smoke Detector | 0.00025 |  | 0.00025 |  | 0
|  | FHA Analog Heat Detector (Fixed) | 0.00025 |  | 0.00025 |  | 0
|  | RHA Analog Heat Detector (R-O-R) | 0.00025 |  | 0.00025 |  | 0
|  | AIB Analog Smoke Detector Base w/ Isolator | 0.00025 |  | 0.0018 |  | 0
|  | ARB Analog Smoke Detector Base w/ Relay | 0.00025 |  | 0.00025 |  | 0
|  | ASB Analog Smoke Detector Base w/ Sounder | 0.00025 |  | 0.00025 |  | 0
| 0 | Total Standby Current: |  | 0 | Max Alarm: | 0 | 0
| Aux Power (500 mA MAX) | Total # of Devices Available | 60
| 0 | Total # of Devices Used | 0
| Aux Power (300 mA MAX) | [5 empty] | 60
OTHER ( Enter device Model and Current Draw Below )
0
60
| .300 | Total Standby Current: |  | 0 | Total Alarm: | 0
| Notification Appliances | [5 empty] | 0
OTHER ( Enter device Model and Current Draw Below )
| Total Notification Appliance |  |  |  | Total Alarm: | 0
System Totals (Circuit totals appearing in Red exceed panel capacity for that circuit(s)
| Circuit |  | Standby |  | Alarm
| Fire Alarm Control Panel |  | 0.172 |  | 0.272
| Fire Alarm Panel Components |  | 0 |  | 0
| Addressable Modules & Short Circuit Isolator |  | 0 |  | 0
| Initiating Devices & Bases |  | 0 |  | 0
| Auxiliary Power Devices |  | 0 |  | 0
| Notification Appliances |  | 0 |  | 0
|  | Total Standby Current Calculated | 0.172
|  | X Standby Hours Required (24) | 24
|  | Standby Amp-Hours Calculated | 4.128
|  | Total Alarm Current | 0.272
|  | X Alarm Minutes Required (5) / 60 | 0.083333
|  | Alarm Amp-Hours Calculated | 0.022667
|  | Total Amp-Hours Calculated | 4.1507
|  | X Derating Factor of 1.2 | 1.2
|  | Minimum Battery Size Calculated | 4.9808
Select the next larger battery size than the calculated total.
|  | Enter Battery Size Selected: | 0 |  | (Amp-Hours)
Device Database (Cannot Be Edited)
Fire Alarm Control Panels
Addressable Devices
|  | #1430800 PSA Analog Photoelectric Smoke Detector | 0.00025 | 0.00025
|  | #1430801 PSHA Analog Combination Photoelectric Smoke & Heat Detector | 0.00025 | 0.00025
|  | #1430802 DSA Analog Duct Smoke Detector | 0.00025 | 0.00025
|  | #1430803 FHA Analog Heat Detector (Fixed) | 0.00025 | 0.00025
|  | #1430804 RHA Analog Heat Detector (R-O-R) | 0.00025 | 0.00025
|  | #1430805 AB-4 Analog Smoke Detector Base - 4 inch | 0.00025 | 0.00025
|  | #1430806 AB-6 Analog Smoke Detector Base - 6 inch | 0.00025 | 0.00025
|  | #1430807 AIB Analog Smoke Detector Base w/ Isolator | 0.00025 | 0.0018
|  | #1430808 ARB Analog Smoke Detector Base w/ Relay | 0.00025 | 0.00025
|  | #1430809 ASB Analog Smoke Detector Base w/ Sounder | 0.00025 | 0.00025
Addressable Modules & Short Circuit Isolator
|  | MCM Mini Contact Module | 0.00025 | 0.00025
|  | SCM-4 Single Contact Module | 0.00025 | 0.00025
|  | DCM-4 Dual Contact Module | 0.00025 | 0.00025
|  | CIZM-4 Conventional Input Zone Module | 0.00025 | 0.00025
|  | TRM-4 Twin Relay Module | 0.00025 | 0.00025
|  | MOM-4 Monitored Output Module | 0.00025 | 0.00025
|  | SCI Short Circuit Isolator | 0.00025 | 0.0018
|  | PFC-8060 60 Point Analog Addressable Panel | 0.172 | 0.272
|  | PFC-8500 127 Point Analog Addressable Panel | 0.202 | 0.322
|  | LCD-AN LCD Annunciator | 0.035 | 0.065
|  | LED-AN LED Annunciator | 0.035 | 0.075
|  | CIZM-4 Conventional Input Zone Module | 0.0049 | 0.05
|  | MOM-4 Monitored Output Module | 0.0016 | 0.0016
Notification Appliances
|  | 1. SH-1224 (15cd) Strobe / Horn Wall Mount / High Volume | 0 | 0.149
|  | 1. SH-1224 (15cd) Strobe / Horn Wall Mount / Low Volume | 0 | 0.078
|  | 1. SH-1224 (35cd) Strobe / Horn Wall Mount / High Volume | 0 | 0.189
|  | 1. SH-1224 (35cd) Strobe / Horn Wall Mount / Low Volume | 0 | 0.118
|  | 1. SH-1224 (60cd) Strobe / Horn Wall Mount / High Volume | 0 | 0.218
|  | 1. SH-1224 (60cd) Strobe / Horn Wall Mount / Low Volume | 0 | 0.147
|  | 1. SH-1224 (75cd) Strobe / Horn Wall Mount / High Volume | 0 | 0.233
|  | 1. SH-1224 (75cd) Strobe / Horn Wall Mount / Low Volume | 0 | 0.162
|  | 1. SH-1224 (95cd) Strobe / Horn Wall Mount / High Volume | 0 | 0.264
|  | 1. SH-1224 (95cd) Strobe / Horn Wall Mount / Low Volume | 0 | 0.193
|  | 1. SH-1224 (110cd) Strobe / Horn Wall Mount / High Volume | 0 | 0.283
|  | 1. SH-1224 (110cd) Strobe / Horn Wall Mount / Low Volume | 0 | 0.212
|  | 1. SH-24H (110cd) Strobe / Horn Wall Mount High Intensity / High Volume | 0 | 0.253
|  | 1. SH-24H (110cd) Strobe / Horn Wall Mount High Intensity / Low Volume | 0 | 0.177
|  | 1. SH-24H (135cd) Strobe / Horn Wall Mount High Intensity / High Volume | 0 | 0.27
|  | 1. SH-24H (135cd) Strobe / Horn Wall Mount High Intensity / Low Volume | 0 | 0.194
|  | 1. SH-24H (150cd) Strobe / Horn Wall Mount High Intensity / High Volume | 0 | 0.282
|  | 1. SH-24H (150cd) Strobe / Horn Wall Mount High Intensity / Low Volume | 0 | 0.206
|  | 1. SH-24H (177cd) Strobe / Horn Wall Mount High Intensity / High Volume | 0 | 0.31
|  | 1. SH-24H (177cd) Strobe / Horn Wall Mount High Intensity / Low Volume | 0 | 0.234
|  | 1. SH-24H (185cd) Strobe / Horn Wall Mount High Intensity / High Volume | 0 | 0.318
|  | 1. SH-24H (185cd) Strobe / Horn Wall Mount High Intensity / Low Volume | 0 | 0.242
|  | 1. SH-24H (95cd) Strobe / Horn Wall Mount High Intensity / High Volume | 0 | 0.243
|  | 1. SH-24H (95cd) Strobe / Horn Wall Mount High Intensity / Low Volume | 0 | 0.167
|  | 2. SL-1224 (15cd) Strobe Only Wall Mount | 0 | 0.061
|  | 2. SL-1224 (35cd) Strobe Only Wall Mount | 0 | 0.101
|  | 2. SL-1224 (60cd) Strobe Only Wall Mount | 0 | 0.131
|  | 2. SL-1224 (75cd) Strobe Only Wall Mount | 0 | 0.145
|  | 2. SL-1224 (95cd) Strobe Only Wall Mount | 0 | 0.176
|  | 2. SL-1224 (110cd) Strobe Only Wall Mount | 0 | 0.196
|  | 2. SL-24H (110cd) Strobe Only Wall Mount High Intensity | 0 | 0.161
|  | 2. SL-24H (135cd) Strobe Only Wall Mount High Intensity | 0 | 0.178
|  | 2. SL-24H (150cd) Strobe Only Wall Mount High Intensity | 0 | 0.19
|  | 2. SL-24H (177cd) Strobe Only Wall Mount High Intensity | 0 | 0.218
|  | 2. SL-24H (185cd) Strobe Only Wall Mount High Intensity | 0 | 0.226
|  | 2. SL-24H (95cd) Strobe Only Wall Mount High Intensity | 0 | 0.151
|  | 3. SH-1224-WP (15cd) Weather-Proof Strobe / Horn Wall Mount / High Volume | 0 | 0.172
|  | 3. SH-1224-WP (15cd) Weather-Proof Strobe / Horn Wall Mount / Low Volume | 0 | 0.116
|  | 3. SH-1224-WP (35cd) Weather-Proof Strobe / Horn Wall Mount / High Volume | 0 | 0.203
|  | 3. SH-1224-WP (35cd) Weather-Proof Strobe / Horn Wall Mount / Low Volume | 0 | 0.151
|  | 3. SH-1224-WP (60cd) Weather-Proof Strobe / Horn Wall Mount / High Volume | 0 | 0.236
|  | 3. SH-1224-WP (60cd) Weather-Proof Strobe / Horn Wall Mount / Low Volume | 0 | 0.187
|  | 3. SH-1224-WP (75cd) Weather-Proof Strobe / Horn Wall Mount / High Volume | 0 | 0.233
|  | 3. SH-1224-WP (75cd) Weather-Proof Strobe / Horn Wall Mount / Low Volume | 0 | 0.206
|  | 3. SH-1224-WP (95cd) Weather-Proof Strobe / Horn Wall Mount / High Volume | 0 | 0.254
|  | 3. SH-1224-WP (95cd) Weather-Proof Strobe / Horn Wall Mount / Low Volume | 0 | 0.227
|  | 3. SH-1224-WP (110cd) Weather-Proof Strobe / Horn Wall Mount / High Volume | 0 | 0.268
|  | 3. SH-1224-WP (110cd) Weather-Proof Strobe / Horn Wall Mount / Low Volume | 0 | 0.241
|  | 4. SL-1224 WP (15cd) Weather-Proof Strobe Only Wall Mount | 0 | 0.129
|  | 4. SL-1224 WP (35cd) Weather-Proof Strobe Only Wall Mount | 0 | 0.16
|  | 4. SL-1224 WP (60cd) Weather-Proof Strobe Only Wall Mount | 0 | 0.193
|  | 4. SL-1224 WP (75 cd) Weather-Proof Strobe Only Wall Mount | 0 | 0.19
|  | 4. SL-1224 WP (95cd) Weather-Proof Strobe Only Wall Mount | 0 | 0.211
|  | 4. SL-1224 WP (110cd) Weather-Proof Strobe Only Wall Mount | 0 | 0.225
|  | 5. SHB24-75 (75cd) Weather-Proof Strobe / Horn Wall Mount | 0 | 0.195
|  | 5. SLB24-75 (75cd) Weather-Proof Strobe Only Wall Mount | 0 | 0.167
|  | 6. SH24C-177 (177cd) Strobe / Horn Ceiling Mount / High Volume | 0 | 0.419
|  | 6. SH24C-177 (177cd) Strobe / Horn Ceiling Mount / Low Volume | 0 | 0.266
|  | 6. SH24C-3075110 (30cd) Strobe / Horn Ceiling Mount / High Volume | 0 | 0.16
|  | 6. SH24C-3075110 (30cd) Strobe / Horn Ceiling Mount / Low Volume | 0 | 0.108
|  | 6. SH24C-3075110 (75cd) Strobe / Horn Ceiling Mount / High Volume | 0 | 0.218
|  | 6. SH24C-3075110 (75cd) Strobe / Horn Ceiling Mount / Low Volume | 0 | 0.148
|  | 6. SH24C-3075110 (110cd) Strobe / Horn Ceiling Mount / High Volume | 0 | 0.273
|  | 6. SH24C-3075110 (110cd) Strobe / Horn Ceiling Mount / Low Volume | 0 | 0.183
|  | 7. SL24C-177 (177cd) Strobe / Horn Ceiling Mount | 0 | 0.26
|  | 7. SL24C-3075110 (110cd) Strobe / Horn Ceiling Mount | 0 | 0.16
|  | 7. SL24C-3075110 (30cd) Strobe / Horn Ceiling Mount | 0 | 0.085
|  | 7. SL24C-3075110 (75cd) Strobe / Horn Ceiling Mount | 0 | 0.139
|  | 8. H-1224 Horn Only / High Volume | 0 | 0.087
|  | 8. H-1224 Horn Only / Low Volume | 0 | 0.016
|  | 8. HP-25 T Wall Mount Mini Horn | 0 | 0.016
|  | 8. MH-1224 Wall Mount Mini Horn | 0 | 0.015
|  | 9. SMD10-3A Sync Module | 0 | 0.034
|  | GMS24-15/75-Z Horn Circuit (Split) | 0 | 0.038
|  | GMS24-15/75-Z Horn/Strobe Synchable | 0 | 0.168
|  | GMS24-15/75-Z Strobe Circuit (Split) | 0 | 0.13
|  | GMS24-30 Horn Circuit (Split) | 0 | 0.038
|  | GMS24-30 Horn/Strobe | 0 | 0.131
|  | GMS24-30 Strobe Circuit (Split) | 0 | 0.093
|  | GMS24-30/75 Horn Circuit (Split) | 0 | 0.038
|  | GMS24-30/75 Horn/Strobe | 0 | 0.18
|  | GMS24-30/75 Strobe Circuit (Split) | 0 | 0.142
|  | GMS24-60 Horn Circuit (Split) | 0 | 0.038
|  | GMS24-60 Horn/Strobe | 0 | 0.153
|  | GMS24-60 Strobe Circuit (Split) | 0 | 0.115
|  | GX90-4 Mini Horn | 0 | 0.015
|  | GX91 Mini Horn | 0 | 0.017
|  | GX93 Temporal Mini Horn | 0 | 0.025
|  | HS24-110 Horn Circuit (Split) | 0 | 0.03
|  | HS24-110 Horn/Strobe | 0 | 0.14
|  | HS24-110 Strobe Circuit (Split) | 0 | 0.11
|  | HS24-15 Horn Circuit (Split) | 0 | 0.03
|  | HS24-15 Horn/Strobe | 0 | 0.075
|  | HS24-15 Strobe Circuit (Split) | 0 | 0.045
|  | HS24-15/75 Horn Circuit (Split) | 0 | 0.03
|  | HS24-15/75 Horn/Strobe | 0 | 0.087
|  | HS24-15/75 Strobe Circuit (Split) | 0 | 0.057
|  | HS24-30 Horn Circuit (Split) | 0 | 0.03
|  | HS24-30 Horn/Strobe | 0 | 0.087
|  | HS24-30 Strobe Circuit (Split) | 0 | 0.057
|  | HS24-60 Horn Circuit (Split) | 0 | 0.03
|  | HS24-60 Horn/Strobe | 0 | 0.114
|  | HS24-60 Strobe Circuit (Split) | 0 | 0.084
|  | HS24-75 Horn Circuit (Split) | 0 | 0.03
|  | HS24-75 Horn/Strobe | 0 | 0.116
|  | HS24-75 Strobe Circuit (Split) | 0 | 0.086
|  | SPKE4-110 Strobe Circuit | 0 | 0.22
|  | SPKE4-15 Strobe Circuit | 0 | 0.078
|  | SPKE4-15/75-C Strobe Circuit | 0 | 0.115
|  | SPKE4-15/75-W Strobe Circuit | 0 | 0.093
|  | SPKE4-15/75-Z Strobe Circuit | 0 | 0.13
|  | SPKE4-30 Strobe Circuit | 0 | 0.093
|  | SPKE4-30/75 Strobe Circuit | 0 | 0.142
|  | SPKE4-60 Strobe Circuit | 0 | 0.115
|  | SPKE8-110 Strobe Circuit | 0 | 0.22
|  | SPKE8-15 Strobe Circuit | 0 | 0.078
|  | SPKE8-15/75-C Strobe Circuit | 0 | 0.12
|  | SPKE8-15/75-W Strobe Circuit | 0 | 0.093
|  | SPKE8-15/75-Z Strobe Circuit | 0 | 0.13
|  | SPKE8-30 Strobe Circuit | 0 | 0.093
|  | SPKE8-30/75 Strobe Circuit | 0 | 0.142
|  | SPKE8-60 Strobe Circuit | 0 | 0.115
|  | ST24-110 Strobe | 0 | 0.11
|  | ST24-15 Strobe | 0 | 0.045
|  | ST24-15/75 Strobe | 0 | 0.057
|  | ST24-30 Strobe | 0 | 0.057
|  | ST24-60 Strobe | 0 | 0.084
|  | ST24-75 Strobe | 0 | 0.086
|  | WGMS-4-75 Horn Circuit (Split) | 0 | 0.038
|  | WGMS-4-75 Outdoor Horn/Strobe | 0 | 0.143
|  | WGMS-4-75 Strobe Circuit (Split) | 0 | 0.105
|  | ZMS-4 Control Module | 0 | 0.021

## Report (hidden)
PFC-8000 Series Battery Calculation
Company:
Address: |  |  | Project Name:
City: |  |  | Project Number:
State: |  | Zip: | Date:
Phone: |  |  | Designer:
Fax: |  |  | Standby Hours: | 24 | Alarm Mins: | 5
Quantity | Device |  | Standby |  | Alarm
|  |  | Each | Total | Each | Total
Fire Alarm Control Panel
1 | PFC-8060 60 Point Analog Addressable Panel |  | 0.172 | 0.172 | 0.272 | 0.272
Phantom |  | Standy Current: |  | 0.172 | Alarm: | 0.272
Phantom
Fire Alarm Components
|  |  | 0.0 |  | 0.0
Phantom |  | Standby Current: |  | 0 | Alarm: | 0
Phantom
Addressable Modules & Short Circuit Isolator
| MCM Mini Contact Module |  | 0.00025 |  | 0.00025
| SCM-4 Single Contact Module |  | 0.00025 |  | 0.00025
| DCM-4 Dual Contact Module |  | #N/A |  | 0.00025
| CIZM-4 Conventional Input Zone Module |  | 0.00025 |  | 0.00025
| TRM-4 Twin Relay Module |  | 0.00025 |  | 0.00025
| MOM-4 Monitored Output Module |  | 0.00025 |  | 0.00025
| SCI Short Circuit Isolator |  | 0.00025 |  | 0.00025
Phantom |  | Standby Current: |  | 0 | Alarm: | 0
Initiating Devices & Bases
| PSA Analog Photoelectric Smoke Detector |  | 0.00025 |  | 0.00025
| PSHA Analog Combination Photoelectric Smoke & Heat Detector |  | 0.00025 |  | 0.00025
| DSA Analog Duct Smoke Detector |  | 0.00025 |  | 0.00025
| FHA Analog Heat Detector (Fixed) |  | 0.00025 |  | 0.00025
| RHA Analog Heat Detector (R-O-R) |  | 0.00025 |  | 0.00025
| AIB Analog Smoke Detector Base w/ Isolator |  | 0.00025 |  | 0.0018
| ARB Analog Smoke Detector Base w/ Relay |  | 0.00025 |  | 0.00025
| ASB Analog Smoke Detector Base w/ Sounder |  | 0.00025 |  | 0.00025
Phantom | Standby Current: |  |  | 0 | Alarm: | 0
Aux Power (300 mA MAX)
0
0
0
0
| 0 |  | 0 |  | 0
| 0 |  | 0 |  | 0
| 0 |  | 0 |  | 0
| 0 |  | 0 |  | 0
Phantom | Total Aux Power Standby Current: |  |  | 0 | Alarm: | 0
Notification Appliances
0
0
0
0
0
0
0
0
0
0
0
| 0 |  | 0 | 0 | 0
| 0 |  | 0 | 0 | 0
| 0 |  | 0 | 0 | 0
| 0 |  | 0 | 0 | 0
| 0 |  | 0 | 0 | 0
Phantom | Total Notification Appliance Standby Current: |  |  | 0 | Alarm: | 0
Phantom | System Totals
Phantom | Circuit |  | Standby |  | Alarm
Phantom | Fire Alarm Control Panel |  | 0.172 |  | 0.272
Phantom | Fire Alarm Control Panel Components |  | 0 |  | 0
Phantom | Addressable Modules & Short Circuit Isolator |  | 0 |  | 0
Phantom | Initiating Devices & Bases |  | 0 |  | 0
Phantom | Auxiliary Power Devices |  | 0 |  | 0
Phantom | Notification Appliances |  | 0 |  | 0
Phantom |  | Total Standby Current Calculated: | 0.172
Phantom |  | X Standby Hours Required (24) | 24
Phantom |  | Standby Amp-Hours Calculated: | 4.128
Phantom
Phantom |  | Total Alarm Current Calculated: | 0.272
Phantom |  | X Alarm Minutes (5) /60 | 0.083333
Phantom |  | Alarm Amp-Hours Calculated: | 0.022667
Phantom
Phantom |  | Total Amp-Hours Calculated | 4.1507
Phantom |  | X Derating Factor of 1.2 | 1.2
Phantom |  | Minimum Battery Size Calculated | 4.9808
Phantom
Phantom |  | Battery Size Selected: | 0 AH