## EVAX-X70
|  |  | Project Name: |  |  | Standby Hours: | 24
[6 empty] | Alarm Mins: | 15
Potter EVAX Panels Battery & Voltage Drop Calculations |  |  | Installed By: |  |  | Efficiency Factor: | 20%
|  |  | Designed By: |  |  | Wattage Usage: | 100
|  |  | Date: |  |  | Speaker Voltage: | 25v
| Model #: | EVAX-X70
| Panel ID: |  |  |  | User assumes all responsibility to ensure the quantities and current draw values in this worksheet are accurate prior to submittal.
Location:
EVAX Emergency Communication System |  |  |  | Standby (amps) |  | Alarm (amps) |  | 25v | 20%
Qty | Part # | Description |  | Each | Total | Each | Total | 70v | 25%
1 | EVAX-X70 | EVAX-X70- Single Channel, 50W, 25V and 70V Selectable, Amplifier |  | 0.115 | 0.115 | 0.346 | 0.346 |  | 25v
1 | SCA-5070INT | SCA-5070INT, Single Channel, 50W, 25V or 70V Selectable, Internal Amplifier |  | 0.015 | 0.015 | 0.146 | 0.146
|  | Amplifier Load |  | 0 | 0 | 4.7917 | 4.7917 |  | 70v
|  |  |  | Panel Standby: | 0.13 | Panel Alarm: | 5.2837
P-LINK (RS-485) (Both P-Link Circuits Combined) |  |  |  | Standby (amps) |  | Alarm(amps)
Qty | Part # | Description |  | Each | Total | Each | Total
1 | SCA-2525 |  |  | 0.015 | 0.015 | 0.015 | 0.015
1 | SCA-2570 |  |  | 0.015 | 0.015 | 0.015 | 0.015
1 | SCA-5025 |  |  | 0.015 | 0.015 | 0.015 | 0.015
1 | SCA-5070 |  |  | 0.015 | 0.015 | 0.015 | 0.015
1 | SCA-10070 |  |  | 0.015 | 0.015 | 0.015 | 0.015
1 | DCA-5025 |  |  | 0.015 | 0.015 | 0.015 | 0.015
1 | DCA-10025 |  |  | 0.015 | 0.015 | 0.015 | 0.015
1 | RM-1000ECS |  |  | 0.034 | 0.034 | 0.055 | 0.055
1 | CIM-16 |  |  | 0.023 | 0.023 | 0.015 | 0.015
1 | FFT-1000R/L |  |  | 0.015 | 0.015 | 0.023 | 0.023
1 | PSN-1000 |  |  | 0.015 | 0.015 | 0.015 | 0.015
1 | SB-24 |  |  | 0.004 | 0.004 | 0.027 | 0.027
|  |  |  | Total Standby: | 0.326 | Total Alarm: | 5.5237 |  | 1.841
|  |  |  | Standby Hours: | 24 | Alarm Mins: | 15
|  |  |  | AH Required | 7.824 | AH Required | 1.3809
[6 empty] | Total Combined Standby & Alarm AmpHours Required: | 9.2049
[6 empty] | Efficiency Factor: | 20%
[6 empty] | Required Battery AmpHours: | 11.0459
Battery AmpHours Provided:
Note: The cabinet will house two 8 AH or 18 AH batteries. The charging circuit is rated for up to two 55 AH batteries.
Note on I43: 10.6.7.2.1 NFPA 72 Battery calculation shall include a 20% safety margin to the calculated amp-hour rating.

## SCA-2525
|  |  | Project Name: |  |  | Standby Hours: | 24
[6 empty] | Alarm Mins: | 15
Potter SCA-2525 Battery & Voltage Drop Calculations |  |  | Installed By: |  |  | Efficiency Factor: | 20%
|  |  | Designed By: |  |  | Wattage Usage:
Date:
| Model #: | SCA-2525
| Panel ID: |  |  |  | User assumes all responsibility to ensure the quantities and current draw values in this worksheet are accurate prior to submittal.
Location:
FACP |  |  |  | Standby (amps) |  | Alarm (amps) |  | 20%
Qty | Part # | Description |  | Each | Total | Each | Total | 25%
1 | SCA-2525 | Single Channel, 25W, 25V Amplifier PCB |  | 0.058 | 0.058 | 0.608 | 0.608 | 25v
|  | Amplifier Load |  | 0 | 0 | 0 | 0 | 70v
|  |  |  | Total Standby: | 0.058 | Total Alarm: | 0.608 | 0.3088
|  |  |  | Standby Hours: | 24 | Alarm Mins: | 15
|  |  |  | AH Required | 1.392 | AH Required | 0.152
[6 empty] | Total Combined Standby & Alarm AmpHours Required: | 1.544
[6 empty] | Efficiency Factor: | 20%
[6 empty] | Required Battery AmpHours: | 1.8528
Battery AmpHours Provided:
Note: The cabinet will house two 8 AH or 18 AH batteries. The charging circuit is rated for up to two 55 AH batteries.
Note on I27: 10.6.7.2.1 NFPA 72 Battery calculation shall include a 20% safety margin to the calculated amp-hour rating.

## SCA-2570
|  |  | Project Name: |  |  | Standby Hours: | 24
[6 empty] | Alarm Mins: | 15
Potter SCA-2570 Battery & Voltage Drop Calculations |  |  | Installed By: |  |  | Efficiency Factor: | 20%
|  |  | Designed By: |  |  | Wattage Usage:
|  |  | Date: |  |  | Speaker Voltage: | 25v
| Model #: | SCA-2570
| Panel ID: |  |  |  | User assumes all responsibility to ensure the quantities and current draw values in this worksheet are accurate prior to submittal.
Location:
FACP |  |  |  | Standby (amps) |  | Alarm (amps) |  | 20%
Qty | Part # | Description |  | Each | Total | Each | Total | 25%
1 | SCA-2570 | Single Channel, 25W, 25V and 70V Selectable, Amplifier PCB |  | 0.058 | 0.058 | 0.608 | 0.608 | 25v
|  | Amplifier Load |  | 0 | 0 | 0 | 0 | 70v
|  |  |  | Total Standby: | 0.058 | Total Alarm: | 0.608 | 0.3088
|  |  |  | Standby Hours: | 24 | Alarm Mins: | 15
|  |  |  | AH Required | 1.392 | AH Required | 0.152
[6 empty] | Total Combined Standby & Alarm AmpHours Required: | 1.544
[6 empty] | Efficiency Factor: | 20%
[6 empty] | Required Battery AmpHours: | 1.8528
Battery AmpHours Provided:
Note: The cabinet will house two 8 AH or 18 AH batteries. The charging circuit is rated for up to two 55 AH batteries.
Note on I27: 10.6.7.2.1 NFPA 72 Battery calculation shall include a 20% safety margin to the calculated amp-hour rating.

## SCA-5025
|  |  | Project Name: |  |  | Standby Hours: | 24
[6 empty] | Alarm Mins: | 15
Potter SCA-5025 Battery & Voltage Drop Calculations |  |  | Installed By: |  |  | Efficiency Factor: | 20%
|  |  | Designed By: |  |  | Wattage Usage:
Date:
| Model #: | SCA-5025
| Panel ID: |  |  |  | User assumes all responsibility to ensure the quantities and current draw values in this worksheet are accurate prior to submittal.
Location:
FACP |  |  |  | Standby (amps) |  | Alarm (amps) |  | 20%
Qty | Part # | Description |  | Each | Total | Each | Total | 25%
1 | SCA-5025 | Single Channel, 50W, 25V, Amplifier PCB |  | 0.058 | 0.058 | 0.608 | 0.608 | 25v
|  | Amplifier Load |  | 0 | 0 | 0 | 0 | 70v
|  |  |  | Total Standby: | 0.058 | Total Alarm: | 0.608 | 0.3088
|  |  |  | Standby Hours: | 24 | Alarm Mins: | 15
|  |  |  | AH Required | 1.392 | AH Required | 0.152
[6 empty] | Total Combined Standby & Alarm AmpHours Required: | 1.544
[6 empty] | Efficiency Factor: | 20%
[6 empty] | Required Battery AmpHours: | 1.8528
Battery AmpHours Provided:
Note: The cabinet will house two 8 AH or 18 AH batteries. The charging circuit is rated for up to two 55 AH batteries.
Note on I27: 10.6.7.2.1 NFPA 72 Battery calculation shall include a 20% safety margin to the calculated amp-hour rating.

## SCA-5070
|  |  | Project Name: |  |  | Standby Hours: | 24
[6 empty] | Alarm Mins: | 15
Potter SCA-5070 Battery & Voltage Drop Calculations |  |  | Installed By: |  |  | Efficiency Factor: | 20%
|  |  | Designed By: |  |  | Wattage Usage: | 1
|  |  | Date: |  |  | Speaker Voltage: | 25v
| Model #: | SCA-5070
| Panel ID: |  |  |  | User assumes all responsibility to ensure the quantities and current draw values in this worksheet are accurate prior to submittal.
Location:
FACP |  |  |  | Standby (amps) |  | Alarm (amps) |  | 25v | 20%
Qty | Part # | Description |  | Each | Total | Each | Total | 70v | 25%
1 | SCA-5070 | Single Channel, 50W, 25V and 70V Selectable, Amplifier PCB |  | 0.058 | 0.058 | 0.608 | 0.608 |  | 25v
|  | Amplifier Load |  | 0 | 0 |  | 0 |  | 70v
|  |  |  | Total Standby: | 0.058 | Total Alarm: | 0.608 |  | 0.3088
|  |  |  | Standby Hours: | 24 | Alarm Mins: | 15
|  |  |  | AH Required | 1.392 | AH Required | 0.152
[6 empty] | Total Combined Standby & Alarm AmpHours Required: | 1.544
[6 empty] | Efficiency Factor: | 20%
[6 empty] | Required Battery AmpHours: | 1.8528
Battery AmpHours Provided:
Note: The cabinet will house two 8 AH or 18 AH batteries. The charging circuit is rated for up to two 55 AH batteries.
Note on I27: 10.6.7.2.1 NFPA 72 Battery calculation shall include a 20% safety margin to the calculated amp-hour rating.

## SCA-5070INT
|  |  | Project Name: |  |  | Standby Hours: | 24
[6 empty] | Alarm Mins: | 15
Potter SCA-5070 Battery & Voltage Drop Calculations |  |  | Installed By: |  |  | Efficiency Factor: | 20%
|  |  | Designed By: |  |  | Wattage Usage: | 25
|  |  | Date: |  |  | Speaker Voltage: | 25v
| Model #: | SCA-5070INT
| Panel ID: |  |  |  | User assumes all responsibility to ensure the quantities and current draw values in this worksheet are accurate prior to submittal.
Location:
FACP |  |  |  | Standby (amps) |  | Alarm (amps) |  | 25v | 20%
Qty | Part # | Description |  | Each | Total | Each | Total | 70v | 25%
1 | SCA-5070INT | SCA-5070INT, 50W, 25V and 70V Selectable, Amplifier |  | 0.05 | 0.05 | 0.138 | 0.138 |  | 25v
|  | Amplifier Load |  | 0 | 0 | 1.1979 | 1.1979 |  | 70v
|  |  |  | Total Standby: | 0.05 | Total Alarm: | 1.3359 |  | 0.3068
|  |  |  | Standby Hours: | 24 | Alarm Mins: | 15
|  |  |  | AH Required | 1.2 | AH Required | 0.33398
[6 empty] | Total Combined Standby & Alarm AmpHours Required: | 1.534
[6 empty] | Efficiency Factor: | 20%
[6 empty] | Required Battery AmpHours: | 1.8408
Battery AmpHours Provided:
Note: The cabinet will house two 8 AH or 18 AH batteries. The charging circuit is rated for up to two 55 AH batteries.
Note on I27: 10.6.7.2.1 NFPA 72 Battery calculation shall include a 20% safety margin to the calculated amp-hour rating.

## SCA-10070
|  |  | Project Name: |  |  | Standby Hours: | 24
[6 empty] | Alarm Mins: | 15
Potter SCA-10070 Battery & Voltage Drop Calculations |  |  | Installed By: |  |  | Efficiency Factor: | 20%
|  |  | Designed By: |  |  | Wattage Usage: | 100
|  |  | Date: |  |  | Speaker Voltage: | 25v
| Model #: | SCA-10070
| Panel ID: |  |  |  | User assumes all responsibility to ensure the quantities and current draw values in this worksheet are accurate prior to submittal.
Location:
FACP |  |  |  | Standby (amps) |  | Alarm (amps) |  | 20%
Qty | Part # | Description |  | Each | Total | Each | Total | 25%
1 | SCA-10070 | Single Channel, 100W, 25V and 70V Selectable, Amplifier PCB |  | 0.06 | 0.06 | 0.766 | 0.766 | 25v
|  | Amplifier Load |  | 0 | 0 | 4.5833 | 4.5833 | 70v
|  |  |  | Total Standby: | 0.06 | Total Alarm: | 5.3493 | 0.55547
|  |  |  | Standby Hours: | 24 | Alarm Mins: | 15
|  |  |  | AH Required | 1.44 | AH Required | 1.3373
[6 empty] | Total Combined Standby & Alarm AmpHours Required: | 2.7773
[6 empty] | Efficiency Factor: | 20%
[6 empty] | Required Battery AmpHours: | 3.3328
Battery AmpHours Provided:
Note: The cabinet will house two 8 AH or 18 AH batteries. The charging circuit is rated for up to two 55 AH batteries.
Note on I27: 10.6.7.2.1 NFPA 72 Battery calculation shall include a 20% safety margin to the calculated amp-hour rating.

## DCA-5025
|  |  | Project Name: |  |  | Standby Hours: | 24
[6 empty] | Alarm Mins: | 15
Potter DCA-5025 Battery & Voltage Drop Calculations |  |  | Installed By: |  |  | Efficiency Factor: | 20%
|  |  | Designed By: |  |  | Wattage Usage:
|  |  | Date: |  |  | Speaker Voltage: | 25v
| Model #: | DCA-5025
| Panel ID: |  |  |  | User assumes all responsibility to ensure the quantities and current draw values in this worksheet are accurate prior to submittal.
Location:
FACP |  |  |  | Standby (amps) |  | Alarm (amps) |  | 20%
Qty | Part # | Description |  | Each | Total | Each | Total | 25%
1 | DCA-5025 | Dual Channel, 50W, 25V, Amplifier |  | 0.048 | 0.048 | 0.52 | 0.52 | 25v
|  | Amplifier Load |  | 0 | 0 | 0 | 0 | 70v
| 70V-1000 | 70V Extender for DCA Amplifiers |  | 0.002 |  | 0.562 |  | 0.2564
| BUA-1000 | Backup Amplifier for DCA Amplifiers |  | 0.048 |  | 0.052
|  |  |  | Total Standby: | 0.048 | Total Alarm: | 0.52
|  |  |  | Standby Hours: | 24 | Alarm Mins: | 15
|  |  |  | AH Required | 1.152 | AH Required | 0.13
[6 empty] | Total Combined Standby & Alarm AmpHours Required: | 1.282
[6 empty] | Efficiency Factor: | 20%
[6 empty] | Required Battery AmpHours: | 1.5384
Battery AmpHours Provided:
Note: The cabinet will house two 8 AH or 18 AH batteries. The charging circuit is rated for up to two 55 AH batteries.
Note on I29: 10.6.7.2.1 NFPA 72 Battery calculation shall include a 20% safety margin to the calculated amp-hour rating.

## DCA-10025
|  |  | Project Name: |  |  | Standby Hours: | 24
[6 empty] | Alarm Mins: | 15
Potter DCA-10025 Battery & Voltage Drop Calculations |  |  | Installed By: |  |  | Efficiency Factor: | 20%
|  |  | Designed By: |  |  | Wattage Usage:
|  |  | Date: |  |  | Speaker Voltage: | 25v
| Model #: | DCA-10025
| Panel ID: |  |  |  | User assumes all responsibility to ensure the quantities and current draw values in this worksheet are accurate prior to submittal.
Location:
FACP |  |  |  | Standby (amps) |  | Alarm (amps) |  | 25v | 20%
Qty | Part # | Description |  | Each | Total | Each | Total | 70v | 25%
1 | DCA-10025 | Dual Channel, 100W, 25V, Amplifier PCB |  | 0.048 | 0.048 | 0.52 | 0.52 |  | 25v
|  | Amplifier Load |  | 0 | 0 | 0 | 0 |  | 70v
| 70V-1000 | 70V Extender for DCA Amplifiers |  | 0.002 |  | 0.562 |  |  | 0.2564
| BUA-1000 | Backup Amplifier for DCA Amplifiers |  | 0.048 |  | 0.052
|  |  |  | Total Standby: | 0.048 | Total Alarm: | 0.52
|  |  |  | Standby Hours: | 24 | Alarm Mins: | 15
|  |  |  | AH Required | 1.152 | AH Required | 0.13
[6 empty] | Total Combined Standby & Alarm AmpHours Required: | 1.282
[6 empty] | Efficiency Factor: | 20%
[6 empty] | Required Battery AmpHours: | 1.5384
Battery AmpHours Provided:
Note: The cabinet will house two 8 AH or 18 AH batteries. The charging circuit is rated for up to two 55 AH batteries.
Note on I29: 10.6.7.2.1 NFPA 72 Battery calculation shall include a 20% safety margin to the calculated amp-hour rating.

## FFT-1000
|  |  | Project Name: |  |  | Standby Hours: | 24
[6 empty] | Alarm Mins: | 15
Potter FFT-1000 Battery & Voltage Drop Calculations |  |  | Installed By: |  |  | Efficiency Factor: | 20%
Designed By:
Date:
| Model #: | FFT-1000
| Panel ID: |  |  |  | User assumes all responsibility to ensure the quantities and current draw values in this worksheet are accurate prior to submittal.
Location:
FACP |  |  |  | Standby (amps) |  | Alarm (amps) |  | 20%
Qty | Part # | Description |  | Each | Total | Each | Total | 25%
1 | FFT-1000* | Fire Fighter Telephone System w/24 Switches |  | 0.154 | 0.154 | 0.295 | 0.295 | 25v
| FFT-EXP | Fire Fighter Telephone Expander Module |  | 0.056 |  | 0.116 |  | 70v
| FSB-24 | 24 Switch Board |  | 0.004 |  | 0.027 |  | 0.75395
| * FFT-1000 includes 1 FSB-24 |  |  | Total Standby: | 0.154 | Total Alarm: | 0.295
|  |  |  | Standby Hours: | 24 | Alarm Mins: | 15
|  |  |  | AH Required | 3.696 | AH Required | 0.07375
[6 empty] | Total Combined Standby & Alarm AmpHours Required: | 3.7697
[6 empty] | Efficiency Factor: | 20%
[6 empty] | Required Battery AmpHours: | 4.5237
Battery AmpHours Provided:
Note: The cabinet will house two 8 AH or 18 AH batteries. The charging circuit is rated for up to two 55 AH batteries.
Note on B22: The maximum FSB-24 switch boards is 3
Note on I28: 10.6.7.2.1 NFPA 72 Battery calculation shall include a 20% safety margin to the calculated amp-hour rating.

## PSN-1000
|  |  | Project Name: |  |  | Standby Hours: | 24
[6 empty] | Alarm Mins: | 5
PSN-1000(E) Battery & Voltage Drop Calculations |  |  | Installed By: |  |  | Efficiency Factor: | 20%
|  |  | Designed By: |  |  | SLC Type: | Class B
|  |  | Date: |  |  | NAC Source Voltage: | 20.4
| Model #: | PSN-1000(E) |  |  |  | Max Panel Current (amps): | 10
| Panel ID: |  |  |  | User assumes all responsibility to ensure the quantities and current draw values in this worksheet are accurate prior to submittal.
Location:
Addressable Power Supply |  |  |  | Standby (amps) |  | Alarm (amps) |  | Class B
Qty | Part # | Description |  | Each | Total | Each | Total | Class A
1 | PSN-1000(E) | Intelligent Power Expander |  | 0.06 | 0.06 | 0.2 | 0.2 | 20%
|  |  |  | Panel Standby: | 0.06 | Panel Alarm: | 0.2 | 25%
P-LINK (RS-485) |  |  |  | Standby |  | Alarm
| SCA-2525 | Single Channel, 25W, 25V Amp |  | 0.015 |  | 0.015
| SCA-2570 | Single Channel, 25W, 25V and 70V Selectable Amp |  | 0.015 |  | 0.015
| SCA-5025 | Single Channel, 50W, 25V Amp |  | 0.015 |  | 0.015 |  |  |  | add SB-24
| SCA-5070 | Single Channel, 50W, 25V and 70V Selectable Amp |  | 0.015 |  | 0.015
| SCA-5070INT | Single Channel, 50W Internal Amplifier, 25V or 70V Selectable Amp |  | 0.015 |  | 2.534
| SCA-10070 | Single Channel, 100W, 25V and 70V Selectable Amp |  | 0.015 |  | 0.015
| DCA-5025 | Dual Channel, 50W, 25V Amp |  | 0.015 |  | 0.015
| DCA-10025 | Dual Channel, 100W, 25V Amp |  | 0.015 |  | 0.015
| FFT-1000R/L | Fire Fighter Telephone System |  | 0.015 |  | 0.015
| RM-1000ECS | Remote Microphone |  | 0.034 |  | 0.055
| CIM-16 | Contact Input Module |  | 0.018 |  | 0.019
(Maximum current draw on P-Link limited to 1 Amp) |  |  |  | P-LINK Standby: | 0 | P-LINK Alarm: | 0
*Only enter quantity if PLINK power is being used to power devices
NAC Circuits (See NAC Configuration below) |  |  |  |  | Standby (amps) |  | Alarm (amps)
Ckt | Use | Description |  | Class | Total |  | Total | 0.292
1 |  |  |  | Class B | 0 |  | 0 | Aux Power
2 |  |  |  | Class B | 0 |  | 0 | Notification
3 |  |  |  | Class B | 0 |  | 0 | Releasing
4 |  |  |  | Class B | 0 |  | 0 | Door Holders
5 |  |  |  | Class B | 0 |  | 0 | Doors (Low AC Drop)
6 |  |  |  | Class B | 0 |  | 0 | City Tie
|  |  |  | NAC Standby: | 0 | NAC Alarm: | 0 | Unused
| Battery Calculation Summary |  |  |  | Standby (amps) |  | Alarm (amps)
|  |  |  | Panel Current: | 0.06 |  | 0.2
|  |  |  | P-Link Current: | 0 |  | 0
|  |  |  | NAC Circuit Current: | 0 |  | 0
| SLC Loop Type: | Class B |  | Total Standby: | 0.06 | Total Alarm: | 0.2
| Device Addresses Used: | #REF! |  | Standby Hours: | 24 | Alarm Mins: | 5
| Device Addresses Available: | #REF! |  | AH Required: | 1.44 | AH Required: | 0.02
[6 empty] | Total Combined Standby & Alarm AmpHours Required: | 1.46
[6 empty] | Safety Margin: | 20%
1 | [5 empty] | Required Battery AmpHours: | 1.752
Battery AmpHours Provided:
Note: The cabinet will house two 8 AH or 18 AH batteries. The charging circuit is rated for up to two 55 AH batteries.
NAC Circuit Configuration & Voltage Drop
Horn Strobes
NAC 1 |  |  | MAX Circuit Current (amps): | 3 |  | Source Voltage Used (VDC): | 20.4 | Strobes
Horns
Class: | Class B | Usage: |  |  | Description: |  |  | MiniHorns
Other Notification
| Wire Type | Ohms/1000ft | Length 1-Way | Actual Ohms | Max Load (amps) | Volts @ EOL | Min Volts Req'd | SLC Aux Power
| #14 Solid | 3.19 |  | 0 | 0 | 20.4 | 16 | Conv Detectors
PLINK Devices
|  | Circuit Devices |  | Standby (amps) |  | Alarm (amps) |  | User Defined
Qty | Lookup Type | Description |  | Each | Total | Each | Total
[8 empty] | #12 Solid | 2.01
[8 empty] | #12 Stranded | 2.05
[8 empty] | #14 Solid | 3.19
[8 empty] | #14 Stranded | 3.26
|  | User can add devices on the fly | [5 empty] | #16 Solid | 5.08
|  | to these bottom 5 rows | [5 empty] | #16 Stranded | 5.29
|  | (No lookup function) | [5 empty] | #18 Solid | 8.08
[8 empty] | #18 Stranded | 8.45
|  |  |  | Total Standby: | 0 | Total Alarm: | 0
NAC 2 |  |  | MAX Circuit Current (amps): | 3 |  | Source Voltage Used (VDC): | 20.4
Class: | Class B | Usage: |  |  | Description:
| Wire Type | Ohms/1000ft | Length 1-Way | Actual Ohms | Max Load (amps) | Volts @ EOL | Min Volts Req'd
| #14 Solid | 3.19 |  | 0 | 0 | 20.4 | 16
|  | Circuit Devices |  | Standby (amps) |  | Alarm (amps)
Qty | Lookup Type | Description |  | Each | Total | Each | Total
User can add devices on the fly
to these bottom 5 rows
(No lookup function)
|  |  |  | Total Standby: | 0 | Total Alarm: | 0
NAC 3 |  |  | MAX Circuit Current (amps): | 3 |  | Source Voltage Used (VDC): | 20.4
Class: | Class B | Usage: |  |  | Description:
| Wire Type | Ohms/1000ft | Length 1-Way | Actual Ohms | Max Load (amps) | Volts @ EOL | Min Volts Req'd
| #14 Solid | 3.19 |  | 0 | 0 | 20.4 | 16
|  | Circuit Devices |  | Standby (amps) |  | Alarm (amps)
Qty | Lookup Type | Description |  | Each | Total | Each | Total
User can add devices on the fly
to these bottom 5 rows
(No lookup function)
|  |  |  | Total Standby: | 0 | Total Alarm: | 0
NAC Circuit Configuration & Voltage Drop (cont'd)
NAC 4 |  |  | MAX Circuit Current (amps): | 3 |  | Source Voltage Used (VDC): | 20.4
Class: | Class B | Usage: |  |  | Description:
| Wire Type | Ohms/1000ft | Length 1-Way | Actual Ohms | Max Load (amps) | Volts @ EOL | Min Volts Req'd
| #12 Solid | 2.01 |  | 0 | 0 | 20.4 | 16
|  | Circuit Devices |  | Standby (amps) |  | Alarm (amps)
Qty | Lookup Type | Description |  | Each | Total | Each | Total
User can add devices on the fly
to these bottom 5 rows
(No lookup function)
|  |  |  | Total Standby: | 0 | Total Alarm: | 0
NAC 5 |  |  | MAX Circuit Current (amps): | 3 |  | Source Voltage Used (VDC): | 20.4
Class: | Class B | Usage: |  |  | Description:
| Wire Type | Ohms/1000ft | Length 1-Way | Actual Ohms | Max Load (amps) | Volts @ EOL | Min Volts Req'd
| #14 Solid | 3.19 |  | 0 | 0 | 20.4 | 16
|  | Circuit Devices |  | Standby (amps) |  | Alarm (amps)
Qty | Lookup Type | Description |  | Each | Total | Each | Total
User can add devices on the fly
to these bottom 5 rows
(No lookup function)
|  |  |  | Total Standby: | 0 | Total Alarm: | 0
NAC 6 |  |  | MAX Circuit Current (amps): | 3 |  | Source Voltage Used (VDC): | 20.4
Class: | Class B | Usage: |  |  | Description:
| Wire Type | Ohms/1000ft | Length 1-Way | Actual Ohms | Max Load (amps) | Volts @ EOL | Min Volts Req'd
| #12 Solid | 2.01 |  | 0 | 0 | 20.4 | 16
|  | Circuit Devices |  | Standby (amps) |  | Alarm (amps)
Qty | Lookup Type | Description |  | Each | Total | Each | Total
User can add devices on the fly
to these bottom 5 rows
(No lookup function)
|  |  |  | Total Standby: | 0 | Total Alarm: | 0
Note on I56: 10.6.7.2.1 NFPA 72 Battery calculation shall include a 20% safety margin to the calculated amp-hour rating.
Note on I68: Enter the lowest minimum voltage required to operate any of the devices on this circuit.
Note on I89: Enter the lowest minimum voltage required to operate any of the devices on this circuit.
Note on I110: Enter the lowest minimum voltage required to operate any of the devices on this circuit.
Note on I134: Enter the lowest minimum voltage required to operate any of the devices on this circuit.
Note on I155: Enter the lowest minimum voltage required to operate any of the devices on this circuit.
Note on I176: Enter the lowest minimum voltage required to operate any of the devices on this circuit.

## Device Database (hidden)
Horn Strobes
(Current draws listed are 2400/3000HZ Temporal audible setting)
Description | Standby | Alarm
Potter HS-24, 15cd, Hi db | 0 | 0.07
Potter HS-24, 30cd, Hi db | 0 | 0.086
Potter HS-24, 60cd, Hi db | 0 | 0.125
Potter HS-24, 75cd, Hi db | 0 | 0.144
Potter HS-24, 110cd, Hi db | 0 | 0.189
Potter HS24-177,177cd, Hi db | 0 | 0.241
Potter CHS-24, 15cd, Hi db | 0 | 0.143
Potter CHS-24, 30cd, Hi db | 0 | 0.143
Potter CHS-24, 75cd, Hi db | 0 | 0.223
Potter CHS-24. 95cd, Hi db | 0 | 0.243
Potter CHS-24, 115cd, Hi db | 0 | 0.313
Potter CHS-24, 150cd, Hi db | 0 | 0.344
Potter CHS-24A, 15cd, Hi db | 0 | 0.75
Potter CHS-24A, 30cd, Hi db | 0 | 0.92
Potter CHS-24A, 60cd, Hi db | 0 | 0.141
Potter CHS-24A, 75cd, Hi db | 0 | 0.173
Potter CHS-24A, 110cd, Hi db | 0 | 0.206
Potter CHS-24B,CHS-24G,CHS-24R, 15cd, Hi db | 0 | 0.133
Potter CHS-24B,CHS-24G,CHS-24R, 30cd, Hi db | 0 | 0.158
Potter CHS-24B,CHS-24G,CHS-24R, 60cd, Hi db | 0 | 0.231
Potter CHS-24B,CHS-24G,CHS-24R, 75cd, Hi db | 0 | 0.271
Potter CHS-24B,CHS-24G,CHS-24R, 110cd, Hi db | 0 | 0.338
Potter CCHS-24A,CCHS-24B,CCHS-24G, 15cd, Hi db | 0 | 0.147
Potter CCHS-24A,CCHS-24B,CCHS-24G, 30cd, Hi db | 0 | 0.147
Potter CCHS-24A,CCHS-24B,CCHS-24G, 75cd, Hi db | 0 | 0.162
Potter CCHS-24A,CCHS-24B,CCHS-24G, 95cd, Hi db | 0 | 0.228
Potter CCHS-24A,CCHS-24B,CCHS-24G, 115cd, Hi db | 0 | 0.235
Potter CCHS-24R, 15cd, Hi db | 0 | 0.147
Potter CCHS-24R, 30cd, Hi db | 0 | 0.147
Potter CCHS-24R, 75cd, Hi db | 0 | 0.235
Potter CCHS-24R, 95cd, Hi db | 0 | 0.306
Potter CCHS-24R, 115cd, Hi db | 0 | 0.336
Potter HS-24-WP, HSLP-24-WP 75cd, Hi db | 0 | 0.198
Potter LFHS-15 Temporal 3 Normal db | 0 | 0.124
Potter LFHS-15 Temporal 3 Loud db | 0 | 0.182
Potter LFHS-15 Temporal 4 Normal db | 0 | 0.195
Potter LFHS-15 Temporal 4 Loud db | 0 | 0.291
Potter LFHS-110 Temporal 3 Normal db | 0 | 0.28
Potter LFHS-110 Temporal 3 Loud db | 0 | 0.326
Potter LFHS-110 Temporal 4 Normal db | 0 | 0.384
Potter LFHS-110 Temporal 4 Loud db | 0 | 0.474
Potter LFHS-177 Temporal 3 Normal db | 0 | 0.365
Potter LFHS-177 Temporal 3 Loud db | 0 | 0.393
Potter LFHS-177 Temporal 4 Normal db | 0 | 0.427
Potter LFHS-177 Temporal 4 Loud db | 0 | 0.525
Potter CHS-24A-WP,CHSLP-24A-WP 75cd, Hi db | 0 | 0.198
CHS-24B-WP,CHS-24G-WP,CSH-24R-WP, 75cd, Hi db | 0 | 0.192
CHSLP-24B-WP,CHSLP-24G-WP,CHSLP-24R-WP, 75cd, Hi db | 0 | 0.192
Potter SH-1224 15cd, Hi db | 0 | 0.149
Potter SH-1224 15cd, Med db | 0 | 0.092
Potter SH-1224 15cd, Lo db | 0 | 0.08
Potter SH-1224 35cd, Hi db | 0 | 0.189
Potter SH-1224 35cd, Med db | 0 | 0.132
Potter SH-1224 35cd, Lo db | 0 | 0.12
Potter SH-1224 60cd, Hi db | 0 | 0.218
Potter SH-1224 60cd, Med db | 0 | 0.161
Potter SH-1224 60cd, Lo db | 0 | 0.149
Potter SH-1224 75cd, Hi db | 0 | 0.233
Potter SH-1224 75cd, Med db | 0 | 0.176
Potter SH-1224 75cd, Lo db | 0 | 0.164
Potter SH-1224 95cd, Hi db | 0 | 0.264
Potter SH-1224 95cd, Med db | 0 | 0.207
Potter SH-1224 95cd, Lo db | 0 | 0.195
Potter SH-1224 110cd, Hi db | 0 | 0.283
Potter SH-1224 110cd, Med db | 0 | 0.226
Potter SH-1224 110cd, Lo db | 0 | 0.214
Potter SH-1224WP 15cd, Hi db | 0 | 0.303
Potter SH-1224WP 15cd, Med db | 0 | 0.21
Potter SH-1224WP 15cd, Lo db | 0 | 0.182
Potter SH-1224WP 35cd, Hi db | 0 | 0.338
Potter SH-1224WP 35cd, Med db | 0 | 0.245
Potter SH-1224WP 35cd, Lo db | 0 | 0.217
Potter SH-1224WP 60cd, Hi db | 0 | 0.374
Potter SH-1224WP 60cd, Med db | 0 | 0.281
Potter SH-1224WP 60cd, Lo db | 0 | 0.253
Potter SH-1224WP 75cd, Hi db | 0 | 0.393
Potter SH-1224WP 75cd, Med db | 0 | 0.3
Potter SH-1224WP 75cd, Lo db | 0 | 0.272
Potter SH-1224WP 95cd, Hi db | 0 | 0.414
Potter SH-1224WP 95cd, Med db | 0 | 0.321
Potter SH-1224WP 95cd, Lo db | 0 | 0.293
Potter SH-1224WP 110cd, Hi db | 0 | 0.428
Potter SH-1224WP 110cd, Med db | 0 | 0.335
Potter SH-1224WP 110cd, Lo db | 0 | 0.307
Potter SH-24H 95cd, Hi db | 0 | 0.238
Potter SH-24H 95cd, Med db | 0 | 0.181
Potter SH-24H 95cd, Lo db | 0 | 0.169
Potter SH-24H 110cd, Hi db | 0 | 0.248
Potter SH-24H 110cd, Med db | 0 | 0.191
Potter SH-24H 110cd, Lo db | 0 | 0.179
Potter SH-24H 135cd, Hi db | 0 | 0.265
Potter SH-24H 135cd, Med db | 0 | 0.208
Potter SH-24H 135cd, Lo db | 0 | 0.196
Potter SH-24H 150cd, Hi db | 0 | 0.277
Potter SH-24H 150cd, Med db | 0 | 0.22
Potter SH-24H 150cd, Lo db | 0 | 0.208
Potter SH-24H 177cd, Hi db | 0 | 0.305
Potter SH-24H 177cd, Med db | 0 | 0.248
Potter SH-24H 177cd, Lo db | 0 | 0.236
Potter SH-24H 185cd, Hi db | 0 | 0.313
Potter SH-24H 185cd, Med db | 0 | 0.256
Potter SH-24H 185cd, Lo db | 0 | 0.244
Potter SH-24H-WP 95cd, Hi db | 0 | 0.238
Potter SH-24H-WP 95cd, Med db | 0 | 0.181
Potter SH-24H-WP 95cd, Lo db | 0 | 0.169
Potter SH-24H-WP 110cd, Hi db | 0 | 0.248
Potter SH-24H-WP 110cd, Med db | 0 | 0.191
Potter SH-24H-WP 110cd, Lo db | 0 | 0.179
Potter SH-24H-WP 135cd, Hi db | 0 | 0.265
Potter SH-24H-WP 135cd, Med db | 0 | 0.208
Potter SH-24H-WP 135cd, Lo db | 0 | 0.196
Potter SH-24H-WP 150cd, Hi db | 0 | 0.277
Potter SH-24H-WP 150cd, Med db | 0 | 0.22
Potter SH-24H-WP 150cd, Lo db | 0 | 0.208
Potter SH-24H-WP 177cd, Hi db | 0 | 0.305
Potter SH-24H-WP 177cd, Med db | 0 | 0.248
Potter SH-24H-WP 177cd, Lo db | 0 | 0.236
Potter SH-24H-WP 185cd, Hi db | 0 | 0.313
Potter SH-24H-WP 185cd, Med db | 0 | 0.256
Potter SH-24H-WP 185cd, Lo db | 0 | 0.244
Potter SH24C-3075110 30cd, Hi db | 0 | 0.16
Potter SH24C-3075110 30cd, Lo db | 0 | 0.138
Potter SH24C-3075110 75cd, Hi db | 0 | 0.218
Potter SH24C-3075110 75cd, Lo db | 0 | 0.201
Potter SH24C-3075110 110cd, Hi db | 0 | 0.273
Potter SH24C-3075110 110cd, Lo db | 0 | 0.256
Potter SH24C-177, 177cd, Hi db | 0 | 0.419
Potter SH24C-177, 177cd, Lo db | 0 | 0.402
Gentex GHSLF-15 Temporal 3 Normal db | 0 | 0.124
Gentex GHSLF-15 Temporal 3 Loud db | 0 | 0.182
Gentex GHSLF-15 Temporal 4 Normal db | 0 | 0.195
Gentex GHSLF-15 Temporal 4 Loud db | 0 | 0.291
Gentex GHSLF-110 Temporal 3 Normal db | 0 | 0.28
Gentex GHSLF-110 Temporal 3 Loud db | 0 | 0.326
Gentex GHSLF-110 Temporal 4 Normal db | 0 | 0.384
Gentex GHSLF-110 Temporal 4 Loud db | 0 | 0.474
Gentex GHSLF-177 Temporal 3 Normal db | 0 | 0.365
Gentex GHSLF-177 Temporal 3 Loud db | 0 | 0.393
Gentex GHSLF-177 Temporal 4 Normal db | 0 | 0.427
Gentex GHSLF-177 Temporal 4 Loud db | 0 | 0.525
Strobes
Description | Standby | Alarm
Potter S-24 Strobe, 15cd | 0 | 0.042
Potter S-24 Strobe, 30cd | 0 | 0.058
Potter S-24 Strobe, 60cd | 0 | 0.097
Potter S-24 Strobe, 75cd | 0 | 0.116
Potter S-24 Strobe, 110cd | 0 | 0.161
Potter S24-177 Strobe, 177cd | 0 | 0.213
Potter CS-24 Strobe, 15cd | 0 | 0.12
Potter CS-24 Strobe, 30cd | 0 | 0.12
Potter CS-24 Strobe, 75cd | 0 | 0.2
Potter CS-24 Strobe, 95cd | 0 | 0.22
Potter CS-24 Strobe, 115cd | 0 | 0.29
Potter CS-24 Strobe, 150cd | 0 | 0.321
Potter S-24-WP Strobe, 75cd | 0 | 0.17
Potter CS-24WA Strobe, 15cd | 0 | 0.047
Potter CS-24WA Strobe, 30cd | 0 | 0.064
Potter CS-24WA Strobe, 60cd | 0 | 0.113
Potter CS-24WA Strobe,75cd | 0 | 0.145
Potter CS-24WA Strobe,110cd | 0 | 0.178
Potter CS-24WB,CS-24WG,CS-24WR Strobe, 15cd | 0 | 0.105
Potter CS-24WB,CS-24WG,CS-24WR Strobe, 30cd | 0 | 0.13
Potter CS-24WB,CS-24WG,CS-24WR Strobe, 60cd | 0 | 0.203
Potter CS-24WB,CS-24WG,CS-24WR Strobe, 75cd | 0 | 0.243
Potter CS-24WB,CS-24WG,CS-24WR Strobe, 110cd | 0 | 0.31
Potter CCS-24A,CCS-24B,CCS-24G Strobe, 15cd | 0 | 0.124
Potter CCS-24A,CCS-24B,CCS-24G Strobe, 30cd | 0 | 0.124
Potter CCS-24A,CCS-24B,CCS-24G Strobe, 75cd | 0 | 0.139
Potter CCS-24A,CCS-24B,CCS-24G Strobe, 95cd | 0 | 0.205
Potter CCS-24A,CCS-24B,CCS-24G Strobe, 115cd | 0 | 0.212
Potter CCS-24R Strobe, 15cd | 0 | 0.124
Potter CCS-24R Strobe, 30cd | 0 | 0.124
Potter CCS-24R Strobe, 75cd | 0 | 0.212
Potter CCS-24R Strobe, 95cd | 0 | 0.283
Potter CCS-24R Strobe, 110cd | 0 | 0.313
Potter CCS-24R Strobe, 75cd | 0 | 0.17
CS-24A-WP,CS-24B-WP,CS-24G-WP,CS-24R-WP Strobe, 75cd | 0 | 0.164
CSLP-24A-WP,CS-24B-WP,CS-24G-WP,CS-24R-WP Strobe, 75cd | 0 | 0.164
Potter SPKSTR-24WLP, 15cd | 0 | 0.078
Potter SPKSTR-24WLP Strobe, 30cd | 0 | 0.096
Potter SPKSTR-24WLP Strobe, 60cd | 0 | 0.137
Potter SPKSTR-24WLP Strobe, 75cd | 0 | 0.18
Potter SPKSTR-24WLP Strobe, 110cd | 0 | 0.224
Potter SPKSTR-24CLP Strobe 15cd | 0 | 0.12
Potter SPKSTR-24CLP Strobe, 30cd | 0 | 0.12
Potter SPKSTR-24CLP Strobe, 75cd | 0 | 0.2
Potter SPKSTR-24CLP Strobe, 95cd | 0 | 0.22
Potter SPKSTR-24CLP Strobe, 115cd | 0 | 0.29
Potter CSPKSTR-24A Strobe, 15/75cd | 0 | 0.148
Potter CSPKSTR-24B Strobe, 15/75cd | 0 | 0.28
Potter CSPKSTR-24G Strobe, 15/75cd | 0 | 0.36
Potter CSPKSTR-24R Strobe, 15/75cd | 0 | 0.397
Potter SL-1224 Strobe 15cd | 0 | 0.061
Potter SL-1224 Strobe 35cd | 0 | 0.101
Potter SL-1224 Strobe 60cd | 0 | 0.131
Potter SL-1224 Strobe 75cd | 0 | 0.145
Potter SL-1224 Strobe 95cd | 0 | 0.176
Potter SL-1224 Strobe 110cd | 0 | 0.196
Potter SL-1224WP Strobe 15cd | 0 | 0.1
Potter SL-1224WP Strobe 35cd | 0 | 0.135
Potter SL-1224WP Strobe 60cd | 0 | 0.171
Potter SL-1224WP Strobe 75cd | 0 | 0.19
Potter SL-1224WP Strobe 95cd | 0 | 0.211
Potter SL-1224WP Strobe 110cd | 0 | 0.225
Potter SL-24H Strobe 95cd | 0 | 0.151
Potter SL-24H Strobe 110cd | 0 | 0.161
Potter SL-24H Strobe 135cd | 0 | 0.178
Potter SL-24H Strobe 150cd | 0 | 0.19
Potter SL-24H Strobe 177cd | 0 | 0.218
Potter SL-24H Strobe 185cd | 0 | 0.226
Potter SL-24H-WP Strobe 95cd | 0 | 0.151
Potter SL-24H-WP Strobe 110cd | 0 | 0.161
Potter SL-24H-WP Strobe 135cd | 0 | 0.178
Potter SL-24H-WP Strobe 150cd | 0 | 0.19
Potter SL-24H-WP Strobe 177cd | 0 | 0.218
Potter SL-24H-WP Strobe 185cd | 0 | 0.226
Potter SL24C-3075110 Strobe 30cd | 0 | 0.116
Potter SL24C-3075110 Strobe 75cd | 0 | 0.172
Potter SL24C-3075110 Strobe 110cd | 0 | 0.234
Potter SL24C-177 Strobe 177cd | 0 | 0.347
Gentex GES3-24 Strobe, 15cd | 0 | 0.042
Gentex GES3-24 Strobe, 30cd | 0 | 0.058
Gentex GES3-24 Strobe, 60cd | 0 | 0.097
Gentex GES3-24 Strobe, 75cd | 0 | 0.116
Gentex GES3-24 Strobe, 110cd | 0 | 0.161
Gentex GES24-177 Strobe, 177cd | 0 | 0.213
Gentex GCS24 Strobe, 15cd | 0 | 0.12
Gentex GCS24 Strobe, 30cd | 0 | 0.12
Gentex GCS24 Strobe, 75cd | 0 | 0.2
Gentex GCS24 Strobe, 95cd | 0 | 0.22
Gentex GCS24 Strobe, 115cd | 0 | 0.29
Gentex GCS24 Strobe, 150cd | 0 | 0.321
Gentex WGES24-75 Strobe, 75cd | 0 | 0.17
Gentex GESA24 Strobe, 15cd | 0 | 0.047
Gentex GESA24 Strobe, 30cd | 0 | 0.064
Gentex GESA24 Strobe, 60cd | 0 | 0.113
Gentex GESA24 Strobe,75cd | 0 | 0.145
Gentex GESA24 Strobe,110cd | 0 | 0.178
Gentex GESB24, GESG24, GESR24 Strobe, 15cd | 0 | 0.105
Gentex GESB24, GESG24, GESR24 Strobe, 30cd | 0 | 0.13
Gentex GESB24, GESG24, GESR24 Strobe, 60cd | 0 | 0.203
Gentex GESB24, GESG24, GESR24 Strobe, 75cd | 0 | 0.243
Gentex GESB24, GESG24, GESR24 Strobe, 110cd | 0 | 0.31
Gentex GCSA24, GCSB24, GCSG24 Strobe, 15cd | 0 | 0.124
Gentex GCSA24, GCSB24, GCSG24 Strobe, 30cd | 0 | 0.124
Gentex GCSA24, GCSB24, GCSG24 Strobe, 75cd | 0 | 0.139
Gentex GCSA24, GCSB24, GCSG24 Strobe, 95cd | 0 | 0.205
Gentex GCSA24, GCSB24, GCSG24 Strobe, 115cd | 0 | 0.212
Gentex GCSR24 Strobe, 15cd | 0 | 0.124
Gentex GCSR24 Strobe, 30cd | 0 | 0.124
Gentex GCSR24 Strobe, 75cd | 0 | 0.212
Gentex GCSR24 Strobe, 95cd | 0 | 0.283
Gentex GCSR24 Strobe, 110cd | 0 | 0.313
Gentex WGESA24 Strobe, 75cd | 0 | 0.17
Gentex WGESB24, WGESG24, WGESR24 Strobe, 75cd | 0 | 0.164
Gentex SSPK24WLP Strobe, 15cd | 0 | 0.078
Gentex SSPK24WLP Strobe, 30cd | 0 | 0.096
Gentex SSPK24WLP Strobe, 60cd | 0 | 0.137
Gentex SSPK24WLP Strobe, 75cd | 0 | 0.18
Gentex SSPK24WLP Strobe, 110cd | 0 | 0.224
Gentex SSPK24CLP Strobe, 15cd | 0 | 0.12
Gentex SSPK24CLP Strobe, 30cd | 0 | 0.12
Gentex SSPK24CLP Strobe, 75cd | 0 | 0.2
Gentex SSPK24CLP Strobe, 95cd | 0 | 0.22
Gentex SSPK24CLP Strobe, 115cd | 0 | 0.29
Gentex SSPKA24 Strobe, 15/75cd | 0 | 0.148
Gentex SSPKB24 Strobe, 15/75cd | 0 | 0.28
Gentex SSPKG24 Strobe, 15/75cd | 0 | 0.36
Gentex SSPKR24 Strobe, 15/75cd | 0 | 0.397
Horns
Description | Standby | Alarm
Potter H-1224 Horn, Hi db | 0 | 0.087
Potter H-1224 Horn, Med db | 0 | 0.03
Potter H-1224 Horn, Lo db | 0 | 0.018
Potter EH-24 Horn, High db | 0 | 0.029
Potter LFH-24 LF Horn, Temporal 3 Normal db | 0 | 0.0994
Potter LFH-24 LF Horn, Temporal 3 Loud db | 0 | 0.1558
Potter LFH-24 LF Horn, Temporal 4 Normal db | 0 | 0.1001
Potter LFH-24 LF Horn, Temporal 4 Loud db | 0 | 0.1572
Gentex GEH24 Horn, High db | 0 | 0.029
Gentex GHLF LF Horn, Temporal 3 Normal db | 0 | 0.0994
Gentex GHLF LF Horn, Temporal 3 Loud db | 0 | 0.1558
Gentex GHLF LF Horn, Temporal 4 Normal db | 0 | 0.1001
Gentex GHLF LF Horn, Temporal 4 Loud db | 0 | 0.1572
MiniHorns
Description | Standby | Alarm
Potter HP-25T MiniHorn, Syncable | 0 | 0.0164
Potter MH-12/24 MiniHorn | 0 | 0.015
Potter MHT-1224 GX93 Mini Horn | 0 | 0.018
Gentex GX93 Mini Horn | 0 | 0.018
Other Notification
Description | Standby | Alarm
Potter PDC-6-24 Bell | 0 | 0.02
Potter PDC-8-24 Bell | 0 | 0.02
Potter PDC-10-24 Bell | 0 | 0.02
Potter MBA-246 Bell (Obsolete) | 0 | 0.06
Potter MBA-248 Bell (Obsolete) | 0 | 0.06
Potter MBA-2410 Bell (Obsolete) | 0 | 0.06
Federal Signal FHEX Explsn Proof Horn | 0 | 1.2
Federal Signal FSEX & FSEX-HI Explsn Proof Strobe | 0 | 1.9
Clifford and Snell YL6 Explsn Proof Strobe | 0 | 0.54
Clifford and Snell YO6 Explsn Proof Sounder | 0 | 0.35
Clifford and Snell V6 Explsn Proof Strobe 5 Joule | 0 | 0.22
Clifford and Snell V6 Explsn Proof Strobe 10 Joule | 0 | 0.5
Clifford and Snell V6 Explsn Proof Strobe 20 Joule | 0 | 1.1
SLC Aux Power
Description | Standby | Alarm
Potter ARB-6 Det Base w/Relay | 0.005 | 0.05
Potter ASB Det Base w/Sounder | 0.005 | 0.1
Potter CIZM-4 Conv Zone Class A | 0.0049 | 0.05
Potter CIZM-4 Conv Zone Class B | 0.0085 | 0.05
Potter MOM-4 Output Module | 0.0016 | 0.0016
Potter PAD100-NAC Output Module | 0.003 | 0.008
Potter PAD100-ZM Conv Zone Module | 0.015 | 0.06
Potter PAD100-SB Sounder Base | 0.004 | 0.03
Potter PAD300-SB Sounder Base | 0.0055 | 0.042
Potter PAD100-LFSB Sounder Base | 0.0041 | 0.1566
Potter PAD300-LFSB Sounder Base | 0.006 | 0.155
Potter PAD100-DUCTR Duct Det w/ Relay | 0.03 | 0.06
Air Products MS-RA & MS-KA/P/R | 0.045 | 0.09
Conventional Detectors
Description | Standby | Alarm
Potter DSD-P Duct Detector | 0.013 | 0.06
Potter CO-12/24 CO Detector (Obsolete) | 6e-05 | 0.08
Potter CPSD-24V Photo Smoke Det | 0.005 | 0.15
Potter CPSHD-24H Photo/Heat Det | 0.005 | 0.15
Potter CPS-24 Photo Smoke Det | 6e-05 | 0.15
Potter PS-24 Photo Smoke Det (Obsolete) | 4.5e-05 | 0.16
Potter PS-24H Photo/Heat Det (Obsolete) | 4.5e-05 | 0.16
PLINK Devices
Description | Standby | Alarm
DRV-50 LED Power | 0.01 | 0.215
RLY-5 Power | 0.01 | 0.135
LED-16 LED Power | 0.015 | 0.21