## Title Page
Potter Voice Evacuation Systems Battery Calculations
There are separate worksheets/tabs for each of the voice evacuation panels:
PVX Series: Conventional self-contained voice evacuation system
PVC-MP: Master panel for the expandable voice evacuation system*
PVC-DP: Distributed panel for the expandable voice evacuation system*
To complete your battery calculations:
Select the appropriate worksheet, based on panel model.
Enter required standy hours/alarm minutes.
Enter desired battery safety factor. (20% is standard).
Enter system quantities under collumn A.
*Note: When installing a PVC-MP-DP System, complete the PVC-MP worksheet for the master panel, as well as the PVC-DP worksheet for EACH distributed panel.

## PVX Series
Potter PVX Series Battery Calculations
QTY | ITEM | STANDBY CURRENT |  | STANDBY TIME | TOTAL STANDBY PWR (AH) | ALARM CURRENT |  | ALARM TIME | TOTAL ALARM POWER | TOTAL Amp Hour POWER
A |  | B |  | C | D | E |  | F | G | H
|  |  |  | Hours | A x B x C |  |  | Hours | A x D x F | D + G
| 100 / 100E | 0.16 | 0 | 24 | 0 | 0.6 | 0 | 0.25 | 0 | 0
| 50 / 50E | 0.15 | 0 | 24 | 0 | 0.8 | 0 | 0.25 | 0 | 0
| 25 / 25E | 0.18 | 0 | 24 | 0 | 1.1 | 0 | 0.25 | 0 | 0
| PVX-SC | 0.03 | 0 | 24 | 0 | 0.05 | 0 | 0.25 | 0 | 0
| PVX-RM | 0.02 | 0 | 24 | 0 | 0.04 | 0 | 0.25 | 0 | 0
| PVX-ZM | 0.051 | 0 | 24 | 0 | 0.13 | 0 | 0.25 | 0 | 0
| EVX-SL8 | 0.003 | 0 | 24 | 0 | 0.005 | 0 | 0.25 | 0 | 0
| EVX-IL8 | 0.003 | 0 | 24 | 0 | 0.005 | 0 | 0.25 | 0 | 0
| LED/switch | 0 | 0 | 24 | 0 | 0.01 | 0 | 0.25 | 0 | 0
| PVX-OL8 | 0.003 | 0 | 24 | 0 | 0.028 | 0 | 0.25 | 0 | 0
| EVX-ATM | 0.015 | 0 | 24 | 0 | 0.035 | 0 | 0.25 | 0 | 0
| EVX-BA | 0.04 | 0 | 24 | 0 | 0.01 | 0 | 0.25 | 0 | 0
| AL-600 | 0.1 | 0 |  |  | 0.1 | 0
0 | EVX-BAB |  | 0 | 0
|  | SUB TOTALS |  |  | 0 |  |  | SUB TOTAL (H) |  | 0
| ENTER --- | Stby (hours) | 24 | 24 |  |  |  | Safety Factor 20% |  | 1.2
| ENTER --- | Alarm (mins) | 15 | 15
[6 empty] | Total Amp Hour Power |  |  |  | 0
For cabinets containing two amplifiers: Enter both amplifiers in column A on this worksheet. Depending on the final amp hour load it may be possible to power both amplifiers from one set of batteries using the provided battery "Y" Cable. 100W amps can charge up to 24 AH batteries; 25W and 50W amps can charge up to 18AH batteries. If the total calculated amp hour load exceeds the charging limit for one of the amplifiers,then each amplifier must be provided with an individual set of batteries. See the tab below labeled "Y Cable Details" for more information.
Calculation For: |  |  |  |  | Information: |  |  |  | Notes:
OEM / Distributor |  |  |  |  | Date: |  |  |  | batteries will require
Customer |  |  |  |  | Prepared By |  |  |  | external battery box
PO# |  |  |  |  | Fax To: |  |  |  | (not supplied by EVAX)
Job Name |  |  |  |  | Email To:
Panel:
Potter Electric Signal Company hereby disclaims all warranties relating to this software utility, whether expressed or implied, including without limitations any implied warranties of merchantability or fitness for a particular purpose. Potter cannot and will not be liable for any special, incidental, consequential, indirect or similar damages for any reason. It is the sole responsibility of the user to ascertain the accuracy and the reliability of any and all information generated or provided by this software utility.

## MNS
Potter PVX/M Series Battery Calculations
QTY | ITEM | STANDBY CURRENT |  | STANDBY TIME | TOTAL STANDBY PWR (AH) | ALARM CURRENT |  | ALARM TIME | TOTAL ALARM POWER | TOTAL Amp Hour POWER
A |  | B |  | C | D | E |  | F | G | H
|  |  |  | Hours | A x B x C |  |  | Hours | A x D x F | D + G
| 100 / 100E | 0.16 | 0 | 24 | 0 | 0.6 | 0 | 0.25 | 0 | 0
| EVX-RM8 | 0.012 | 0 | 24 | 0 | 0.037 | 0 | 0.25 | 0 | 0
| EVX-SL8 | 0.003 | 0 | 24 | 0 | 0.005 | 0 | 0.25 | 0 | 0
| EVX-IL8 | 0.003 | 0 | 24 | 0 | 0.005 | 0 | 0.25 | 0 | 0
| EVX-OL8 | 0.003 | 0 | 24 | 0 | 0.028 | 0 | 0.25 | 0 | 0
| EVX-ZM | 0.051 | 0 | 24 | 0 | 0.13 | 0 | 0.25 | 0 | 0
| AL-600 | 0.1 | 0 |  |  | 0.1 | 0
0 | EVX-BAB |  | 0 | 0
|  | SUB TOTALS |  |  | 0 |  |  | SUB TOTAL (H) |  | 0
| ENTER --- | Stby (hours) | 24 | 24 |  |  |  | 0.25 |  | 1.2
| ENTER --- | Alarm (mins) | 15 | 15
[6 empty] | Total Amp Hour Power |  |  |  | 0
COLUMN
A |  | Total number of each item in each cabinet
C |  | Number of Hours for Standby Time
Typically: 24, or 60
D |  | Qty x Stand by Current x Stand-By Time = Total Stand-By Power, Column: A x B x C = D
Column: A x B x C = D
F |  | Alarm Time in hours is = to # of minutes / 60
example:15 min / 60 = .25 hours
G |  | Qty x Alarm Current x Alarm Time
Column: A x D x F = G
H |  | Total Stand-By Power + Total Alarm Power
Column: D + G = H
Formula: Total AH Power = Total COLUMN "H" x 1.2 (20% Safety Margin)
Total Amp Hour Power is the Amp Hour rating of each SET OF Batteries for EACH Amplifier
Calculation For: |  |  |  |  | Information: |  |  |  | Notes:
OEM / Distributor |  |  |  |  | Date: |  |  |  | batteries will require
Customer |  |  |  |  | Prepared By |  |  |  | external battery box
PO# |  |  |  |  | Fax To: |  |  |  | (not supplied by EVAX)
Job Name |  |  |  |  | Email To:
Panel:
Potter Electric Signal Company hereby disclaims all warranties relating to this software utility, whether expressed or implied, including without limitations any implied warranties of merchantability or fitness for a particular purpose. Potter Electric cannot and will not be liable for any special, incidental, consequential, indirect or similar damages for any reason.
It is the sole responsibility of the user to ascertain the accuracy and the reliability of any and all information generated or provided by this software utility.

## PVC-MP
Potter PVC-MP Battery Calculations
QTY | ITEM | STANDBY CURRENT |  | STAND BY TIME | TOTAL STANDBY PWR (AH) | ALARM CURRENT |  | ALARM TIME | TOTAL ALARM POWER | TOTAL Amp Hour POWER
A |  | B |  | C | D | E |  | F | G | H
A |  | B |  | C |  | D |  | E
|  |  |  | Hours | A x B x C |  |  | Hours | A x D x F | D + G
1 | PVC-SSC | 0.028 | 0.028 | 24 | 0.672 | 0.028 | 0.028 | 0.25 | 0.007 | 0.679
1 | PVC-MMC | 0.046 | 0.046 | 24 | 1.104 | 0.046 | 0.046 | 0.25 | 0.0115 | 1.1155
1 | PVC-ASC | 0.023 | 0.023 | 24 | 0.552 | 0.033 | 0.033 | 0.25 | 0.00825 | 0.56025
1 | PVC-DCC | 0.083 | 0.083 | 24 | 1.992 | 0.083 | 0.083 | 0.25 | 0.02075 | 2.0128
1 | PVC-PWR | 0.016 | 0.016 | 24 | 0.384 | 0.016 | 0.016 | 0.25 | 0.004 | 0.388
0 | AL-600 | 0.1 | 0 | 24 | 0 | 0.1 | 0 | 0.25 | 0 | 0
| PVC-SSC | 0.028 | 0 | 24 | 0 | 0.028 | 0 | 0.25 | 0 | 0
| PVC-SLC | 0.0002 |  | 24 | 0 | 0.016 |  | 0.25 | 0 | 0
| PVC-FO | 0.051 | 0 | 24 | 0 | 0.051 | 0 | 0.25 | 0 | 0
| MX-FO7 | 0.04 | 0 | 24 | 0 | 0.04 | 0 | 0.25 | 0 | 0
| PVC-II | 0.018 | 0 | 24 | 0 | 0.019 | 0 | 0.25 | 0 | 0
| PVX-ATM | 0.015 | 0 | 24 | 0 | 0.035 | 0 | 0.25 | 0 | 0
| PVX-RM | 0.02 | 0 | 24 | 0 | 0.04 | 0 | 0.25 | 0 | 0
| PVX-SC | 0.03 | 0 | 24 | 0 | 0.05 | 0 | 0.25 | 0 | 0
| PVC-MFP | 0.009 | 0 | 24 | 0 | 0.009 | 0 | 0.25 | 0 | 0
0 | MX-MFH |  |  | 15 |  |  |  | 0
0 | MX-ISO | 0.02 | 0 | 15 | 0 | 0.02 | 0 | 0 | 0 | 0
0 | MX-ISO2 |  | 0 | 15 | 0 |  | 0 | 0 | 0 | 0
0 | MX-IPI |  | 0 | 15 | 0 |  | 0 | 0 | 0 | 0
0 | MX-KS4 |  | 0 | 15 | 0 |  | 0 | 0 | 0 | 0
|  | SUB TOTALS |  |  | 4.704 |  |  | SUB TOTAL (H) |  | 4.7555
| ENTER --- | Stby (hours) | 24 | 24 |  |  |  | Safety Factor 20% |  | 1.2
| ENTER --- | Alarm (mins) | 15 | 15
[6 empty] | Total Amp Hour Power |  |  |  | 5.7066
For cabinets containing two amplifiers: Enter both amplifiers in column A on this worksheet. Depending on the final amp hour load it may be possible to power both amplifiers from one set of batteries using the provided battery "Y" Cable. 100W amps can charge up to 24 AH batteries; 25W and 50W amps can charge up to 18AH batteries. If the total calculated amp hour load exceeds the charging limit for one of the amplifiers,then each amplifier must be provided with an individual set of batteries. See the tab below labeled "Y Cable Details" for more information.
Potter Electric Signal Company hereby disclaims all warranties relating to this software utility, whether expressed or implied, including without limitations any implied warranties of merchantability or fitness for a particular purpose. Potter cannot and will not be liable for any special, incidental, consequential, indirect or similar damages for any reason. It is the sole responsibility of the user to ascertain the accuracy and the reliability of any and all information generated or provided by this software utility.
Calculation For: |  |  |  |  | Information: |  |  |  | Notes:
OEM / Distributor |  |  |  |  | Date: |  |  |  | batteries will require
Customer |  |  |  |  | Prepared By |  |  |  | external battery box
PO# |  |  |  |  | Fax To: |  |  |  | (not supplied by EVAX)
Job Name |  |  |  |  | Email To:
Panel:

## PVC-DP
Potter PVC-DP Battery Calculations
QTY | ITEM | STANDBY CURRENT |  | STAND BY TIME | TOTAL STANDBY PWR (AH) | ALARM CURRENT |  | ALARM TIME | TOTAL ALARM POWER | TOTAL Amp Hour POWER
A |  | B |  | C | D | E |  | F | G | H
A |  | B |  | C |  | D |  | E
|  |  |  | Hours | A x B x C |  |  | Hours | A x D x F | D + G
1 | PVC-AMI | 0.022 | 0.022 | 24 | 0.528 | 0.022 | 0.022 | 0.25 | 0.0055 | 0.5335
1 | PVC-MBK | 0.003 | 0.003 | 24 | 0.072 | 0.031 | 0.031 | 0.25 | 0.00775 | 0.07975
1 | PVC-MBR | 0.031 | 0.031 | 24 | 0.744 | 0.031 | 0.031 | 0.25 | 0.00775 | 0.75175
1 | PVC-DCC | 0.082 | 0.082 | 24 | 1.968 | 0.084 | 0.084 | 0.25 | 0.021 | 1.989
| PVC-MBK | 0.003 | 0 | 24 | 0 | 0.031 | 0 | 0.25 | 0 | 0
| PVX-100E | 0.16 | 0 | 24 | 0 | 0.6 | 0 | 0.25 | 0 | 0
| PVX-50E | 0.15 | 0 | 24 | 0 | 0.8 | 0 | 0.25 | 0 | 0
| PVX-25E | 0.18 | 0 | 24 | 0 | 1.1 | 0 | 0.25 | 0 | 0
| PVX-BA | 0.04 | 0 | 24 | 0 | 0.01 | 0 | 0.25 | 0 | 0
| EVX-BAB |  | 0 | 24 | 0 |  | 0 | 0.25 | 0 | 0
| PVX-ZA | 0.038 | 0 | 24 | 0 | 0.048 | 0 | 0.25 | 0 | 0
| EVX-ZAB | 0 | 0 | 24 | 0 | 0 | 0 | 0.25 | 0 | 0
| MX-INB |  | 0 | 24 | 0 |  | 0 | 0.25 | 0 | 0
| MX-AOR | 0.025 | 0 | 24 | 0 | 0.025 | 0 | 0.25 | 0 | 0
| MX-FPR |  | 0 | 24 | 0 |  | 0 | 0.25 | 0 | 0
| AL-600 | 0.1 | 0 | 24 | 0 | 0.1 | 0 | 0.25 | 0 | 0
| PVC-FO | 0.051 | 0 | 24 | 0 | 0.051 | 0 | 0.25 | 0 | 0
| PVC-FPI | 0.041 | 0 | 24 | 0 | 0.041 | 0 | 0.25 | 0 | 0
|  | SUB TOTALS |  |  | 3.312 |  |  | SUB TOTAL (H) |  | 3.354
| ENTER --- | Stby (hours) | 24 | 24 |  |  |  | Safety Factor 20% |  | 1.2
| ENTER --- | Alarm (mins) | 15 | 15
[6 empty] | Total Amp Hour Power |  |  |  | 4.0248
For cabinets containing two amplifiers: Enter both amplifiers in column A on this worksheet. Depending on the final amp hour load it may be possible to power both amplifiers from one set of batteries using the provided battery "Y" Cable. 100W amps can charge up to 24 AH batteries; 25W and 50W amps can charge up to 18AH batteries. If the total calculated amp hour load exceeds the charging limit for one of the amplifiers,then each amplifier must be provided with an individual set of batteries. See the tab below labeled "Y Cable Details" for more information.
Potter Electric Signal Company hereby disclaims all warranties relating to this software utility, whether expressed or implied, including without limitations any implied warranties of merchantability or fitness for a particular purpose. Potter cannot and will not be liable for any special, incidental, consequential, indirect or similar damages for any reason. It is the sole responsibility of the user to ascertain the accuracy and the reliability of any and all information generated or provided by this software utility.