## Sheet1
PLINK WIRE DISTANCE / WIRE GAUGE CALCULATOR
P-Link max wire resistance is based on load - calculated using the following equation
(Total P-Link Alarm Current) X (Wire Resistance) < 6 Volts
Enter quantity of P-Link Devices On Circuit
Quantity | PLINK - RS 485 Devices |  |  |  | Alarm Current
| RA-6075R | LCD Annunciator |  |  | 0.025
| RA-6500R(F) | Flush Mount LCD Annunciator |  |  | 0.025
| LED-16(F) | Flush Mount LED Annunciator |  |  | 0.025
| LED-16(F) Power | Enter if Power from P-Link |  |  | 0.215
| PSN-1000(E) | Power Expander |  |  | 0.015
| PAD100-SLCE-127 | SLC Expander |  |  | 0.2
| NOHMI-SLCE-127 | SLC Expander |  |  | 0.2 | #12 Solid | 2.01
| RLY-5 | Relay Expander |  |  | 0.035 | #12 Stranded | 2.05
| RLY-5 Power | Enter if Power from P-Link |  |  | 0.135 | #14 Solid | 3.19
| DRV-50 | LED Driver Module |  |  | 0.025 | #14 Stranded | 3.26
| DRV-50 Power | Enter if power from P-Link |  |  | 0.215 | #16 Solid | 5.08
| FCB-1000 | Fire Communications Bridge |  |  | 0.025 | #16 Stranded | 5.29
| FIB-1000 | Fiber Interface Board |  |  | 0.03 | #18 Solid | 8.08
| MC-1000 | Multi-Connect Expander |  |  | 0.01 | #18 Stranded | 8.45
| SPG-1000 | Serial Parallel Gateway |  |  | 0.04
| IDC-6 | Initiating Device Circuit Expander |  |  | 0.02
| IDC-6 Power | Enter if Power from P-Link |  |  | 0.27
| NCE-1000 | Network Card Ethernet |  |  | 0.05
| NCF-1000 | Network Card Fiber |  |  | 0.095
| VM-1000 | Voice Module |  |  | 0.069
| SB-8 | Switch Module |  |  | 0.013
| SB-24 | Switch Module |  |  | 0.027
| LOC-1000 | Local Operating Console |  |  | 0.107
| SCA/DCA Amp | Single or Dual Channel Amplifier |  |  | 0.015
| FFT-1000(R/L) | Fire Fighter Telephone Panel |  |  | 0.015
Select wire type / gauge and enter length - Max 6500'
Wire Type | Ohms/1000ft | Length 1-Way | Actual Ohms
#12 Solid | 2.01 |  | 0
VOLTAGE DROP
TOTAL PLINK ALARM CURRENT X |  | WIRE RESISTANCE |  | MUST BE LESS THAN 6V
0 |  | 0 |  | 0
P-Link - 1 Amp Max Current